## Settings
Project Configuration
;
| Version | Notes | Release Date | Checked | Approved
| 0.1 | Handover | 2016-05-26
| V4版本控制器主要更新内容 | 更新内容： 1）增加了Yaw Pitch Kick功能。 2）增加了第二种基于机舱加速度的最小桨距角查表功能(在dlc1.3额定以下触发，降低额定附近叶根极限载荷)。 3）正常发电工况和极端工况设置了不同的限功率速率.Dlc1.4由于转速低造成轮毂极限载荷Myz,增大限功率速率转速会高一些，桨距角大，降低轮毂Myz载荷。 4）增加了Fast Shutdown过程中的扭矩速率限制。 5）修改了Pitch Kick功能(发电工况下，满足桨距角，扭矩的条件下，超过阈值触发，持续 P_NonLinearDelayAfterTrip+P_LowestTorsionalModeHalfPeriod),触发后在20s内不再触发。 6）增加了基于机舱加速度De-rating功能(在dlc1.3切出风速附近触发，降低大风驱动的极限载荷 Bug exit)。 7）增加了FastShutdown变速率收桨。 8）增加了基于湍流（转速波动）De-rating功能。 9）增加了大风De-rating功能（类似于暴风算法）。 10）增加了基于湍流的桨距角位置限制功能（T_GentlePitchDropSchedule）。 11）增加了大风切出功能。 12）增加了机舱加速度超限故障。 13）修改了GridlossShutdown与FastShutdown的优先级。 14）增加了GridlossShutdown变速率收桨。 15）增加了正常停机的半闭环停机功能; 16) 增加了N4过速故障穿越功能； 17）增加了新的IPC算法; 18) 增加了基于现场的启机功能； 19)添加了柔性转速控制功能，期望降低dlc1.4的偏航Mxy极限（一个周期转速的加速度<0就关闭该功能，主要考虑1/3,2/3处转速的波动导致功能频繁开启关闭，但是这样会使有的工况无法降载，需要结合Pitch功能能，并考虑多工况的触发情况去验证); | 2017-08-15
| AlgorithmSymbols-GW184P60T115BGW90-V4-03 | 1)调整了P_MinimumFinePitch (0deg)， P_OptimalModeGain参数； 2）重新整定了扭矩回路和变桨回路的控制参数，包括PI参数和滤波器参数； 3）调整了EEDOT的阈值，1.2工况不触发PitchKick； 4)开启了T_FinePitchScheduleYaw功能降低1.4工况由于开桨到最小桨距角造成的叶根极限载荷以及dlc2.4的疲劳载荷； 5) 开启了基于湍流的Derating策略,并调整了阈值，保证1.2工况不触发,用于降低dlc1.3的叶根极限载荷； 6) 开启N4过速故障穿越(PitchKick结合故障穿越，避免DLC14过速停机造成偏航Mxy的极限载荷),将N4=1.12Nr,降低DLC2.1叶根极限; 7) 降低扭矩回路和变桨回路3P,6P的衰减程度,衰减6db; | 2017-11-23
| As-GW184P6300T115BGW90-CFII_V4.01.01_03_beta | (1) 最优桨叶角度调整为0deg,调整了扭矩回路和变桨回路的PI参数和滤波器； (2)将安全链停机的变桨速率降低1deg/s,降低dlc2.2工况卡桨停机轮毂Myz. (3)开启动态转速控制可以降低：dlc1.4cb1-006触发大偏航偏差限功率之前轮毂Myz极限值5%;dlc1.4cb1-006偏航Mxy3%; (4) 将P_PitchSanityGeneratorSpeedLevel降低为额定转速，降低三叶片跑飞工况的叶根极限； (5) 源码中将触发PitchKIck的桨距角限定条件设置为MinPitch+0.1deg,在额定附近能及早触发PitchKick,及时收桨; (6) 将PitchKick附加的变桨速率降低到1.7deg/s,降低轮毂Myz和偏航Mxy,同时修改N4过速故障穿越是否停机的变桨速率判断值,dlc1.4 1/3处仍然有停机可能，造不成极限载荷; dlc1.2不能触发功能块： (1) PitchKick; (2)基于湍流的Derating;(3)动态转速控制功能; (4) T_FinePitchScheduleYaw; | 2017-12-19
| As-GW184P6300T115BGW90-CFII_V4.01.03_03_beta | 针对GW90叶片模型 GW184P6300T115KsBGW90V6k0_20171221.prj (1)调整了扭矩回路和变桨回路的PI参数和滤波器参数,最优桨距角0deg; (2)修改源码，在大偏航偏差限功率过程中不触发PitchKick; (3)升容至6.3MW，修改轴功率、最大扭矩、快速停机扭矩查表; (4) 增加参数P_MinWindSpeedForYawErrorFinePitch,保证dlc1.2小风下不触发 T_FinePitchScheduleYaw功能，dlc1.4工况能触发; (5) 开启微分项，降低叶根Mxy; (6) 开启避转速功能,最小转速降低至4rpm; 载荷结果优化： (1) 对于小风无法启机,优化了启机参数 P_StartupWaitPitchangle， P_StartupWaitTime， P_StartupWaitSpeed.修改了PrePowerProduction = (S_GetVsprState() <= VsprPowerProduction) ; (2)触发安全链停机以后，不报出A_PitchFollowingErrorVspr1,A_PitchFollowingError1故障,降低故障率; 现场应用需要主控提供安全链触发标志位CI_SafetySystemTrigger;
| As-GW184P6300T115BGW90-CFII_V4.01.04_04_beta | (1)更新IPC功能; (2) 调整最小桨距角为最优桨距角-1.5deg(-0.02618)，更新最优增益(3.801E+06); 扭矩回路和变桨回路PI参数和滤波器与V3版保持一致； (3)开启避转速功能；开启加阻功能； (4)极限功能块开启: (1) PitchKick+N4过速故障穿越; (2)基于湍流的Derating;(3)动态转速控制功能; (4) T_FinePitchScheduleYaw; (5) 为了叶片早日定版，出于降载考虑，提升最优桨距角为0deg, 更新最优增益(2.972E+06). (6) 考虑机械结构及IPC，设定参数P_CollectivePitchMinAngle为最优桨距角-2deg； (7) 考虑dlc1.4尽可能触发动态转速控制功能，以降低偏航及轮毂载荷，将参数P_EstimatedGenAccAvt修改为1.2s; | 2018-03-21
| As-GW184P6300T115BGW90-CFII_V5.01.01_04_beta(需要验证控制器升级前后对载荷的影响，下一版叶片开发启用) | v4版控制器升级到V5版增加功能： (1) 失速对最小桨距角的限幅； --金强 (2) 更新StartUp逻辑（EnableVspr功能移到Stratup开始阶段）;更新D_DurationStartUpWait条件(增加过滤条件)；- D_DisconnectedSpeedSetpoint, D_GeneratorSpeedSetpoint, P_GenSpeedAtSyncSpeedRequiredTime, P_ConnectionLullDuration.--屈帆 (3)更新derating功能，修复：限功率速率异常问题，触发限功率没有从当前功率下降，偏航偏差故障无法复位问题--马羽龙 (4)大风切出限功率功能改为限转速，目标是扩展或者不扩展切出风速条件下大风下的降载，同时可兼容其它限转速需求.--杨娟霞 (5)Powershoot功能添加-李永明； (6) 发电机转速动态控制功能-李永明； (7) 基于湍流的Derating-(限桨距角)功能优化-杨娟霞； (8)Lidar功能优化,加入Lidar故障和GRT功能-屈帆,田萌； (9)ipc功能优化--陈博宇; (10)优化加阻功能，偏航偏差超过阈值时，关闭加阻功能--刘略； (11)N4过速故障穿越-杨娟霞; (12)P_PitchDeadBand由2改为0.0349,满发标志位有效,偏航偏差超过40deg,AboveRated不使能； 更新torquelimit.h相关代码【*rQmax = SetTorque*rW2 / std::max(rWgCP, 1)】中的1替换为P_GetLowSpeedSyncSpeed()，避免扭矩受限； 增加FinePitchScheduleYaw触发的风速条件P_MinWindSpeedForYawErrorFinePitch；P_FastShutdownTorqueRateLimit改为1500000；马羽龙，杨娟霞 (13)修改A_PitchFollowingErrorVspr激活条件，启机等风角度之前不触发该故障，在触发安全链之后，也不触发该故障，降低故障率;--马羽龙，杨娟霞 (14) 删除变桨速率死去设置；--杨娟霞 | 2018-04-12
| As-GW184P6300T115BGW90-CFII_V5.01.02_05_beta | V5版控制器基础上： (1) 最优桨距角0deg; (2)P_EstimatedGenAccAvt改为1.5； (3)修改了PitchKick和基于湍流的Derating阈值； (4)参数P_MinWindSpeedForYawErrorFinePitch改为8m/s; (5) 优化PitchKick功能，设置PitchKick作用的最长时间 P_NonLinearAcrDyTimeLimit； (6)关闭GeneratorSpeedDynamicControl功能； (7)P_NormalShutdownLullDuration改为0s; (8) 增加了轴功率的读取； (9) 更新D_DisconnectedSpeedSetpoint计算方式； (11) NormalShutdown和 GridlossShutdown变桨兼容变速率方式; (12)加入Lidar故障号； | 2018-05-16
| As-GW184P6300T115BGW90-CFII_V5.01.03_06_beta（碳玻混叶片） | 1)加入基于测量方位角的净空控制，未开启； 2)优化Lidar功能，并开启； 3)最小桨距角取最优桨距角-0.5deg; 4)增加基于风速的功率自适应调整功能，用于暴风切出,开启； 5)新增P_FinePitchScheduleYawAvT变量，T_FinePitchScheduleYaw与T_FinePitchSchedule使用不同的滤波时间常数； 6)优化dll代码，正常停机执行半闭环停机的条件下，初始桨角的给定值由原来的测量桨角改为触发停机时刻的桨角给定值，避免由于给定桨角的突变触发 A_PitchDemandSanityCheck故障; 7)TiltAngle改回7deg以后，dlc1.2的净空不通过，将P_MinimumFinePitch提升到0deg. | 2018-12-17
| V6.01.01版控制器版本升级 | 1）优化PitchKick功能（一旦触发持续1.5s，在触发完成的30s内不能再次触发） 2)更新PowerShoot功能; 3)整理限功率功能和限转速功能;(暴风切出限功率T_HighWindPowerLimitFactorSchedule 暴风切出限转速T_HighWindSpeedLimitFactorSchedule ) 4)更新Lidar功能: 删除在PitchSpeedGainSchedule.h引进Kp系数的操作； 删除在NonLinearAcrDy.h中附加雷达阵风及风剪切功能产生的变桨速率操作 将以上2项中删除的操作集中在Pitchcontrol.h中执行，减少添加雷达功能引起的代码更改工作 增加了 Kp及Ti系数（Pitchcontrol.h中） 垂直风剪切添加了修正系数0.85，将该系数添加在了symbols-para中。 修改了LidarGRT.cpp LidarShearV.cpp LidarShearH.cpp中部分变量名称，规范名称定义。 说明文档见《金风控制器增加LiDAR控制算法修改说明-LiDAR.V0.20190322.docx》 增加P_GRTtoFinePitchRateLimit变量 5）增加噪声控制功能; 7)恢复变桨速率死区设置; 更改A_PitchDemandSanityCheck逻辑,避免暴风切出限转速功能开启故障不触发问题； 增加T_NormalShutdownPitchrate2，正常停机时按照变桨位置和发电机转速2种方式查变桨速率； 修改PitchCorrect，避免触发正常停机时变桨速率跳变问题； | 2019-4-25（杨娟霞）
Section | Project Information
| Project Name | GW3.0MW(S)-TC3
| Project Code | 10016381
| Version | 0.1
| Win32 Build Output Path | Build\LightController\Win32\Debug\Discon.dll
| XML Output Name | AlgorithmSymbols.xml
Section | XML Imports
| External XML | External Workbook | Transform
| .\LightController\Platform\Beckhoff-TwinCAT3\BeckhoffTwinCAT3Symbols.xml | .\LightController\Platform\Beckhoff-TwinCAT2\BeckhoffTwinCAT2Symbols.xlsx | ..\Infrastructure\Source\Main\Generation\TransformExternalImport.xslt
Section | Workbook Contents
| Sheet | Content Type
| State Machine | State
| State Filter | StateFilter
| DISCON Mappings | DisconIo
| DISCON Parameters | Channel
| Auto System | Channel
| Alarm | Channel
| CIO | Channel
| State | Channel
| Param | Channel
| Derived | Channel
| Filters | Table
| Schedules | Table
Section | Alarm System Config
| Alarm Code | Alarm Type_en_GB
| RW | Warning
| RN | Normal Shutdown
| RS | Slow Shutdown
| RG | Grid Loss Shutdown
| RF | Fast Shutdown
| RP | Pitch Battery Shutdown
| RET | Safety Turbine Shutdown
Section | Error Checking
| Error Check | Disabled
..\Infrastructure\Source\Main\Generation\GenerationChecks.xslt
..\Infrastructure\Source\LightController\Generation\GenerationChecks.xslt
Section | Auto-Generated Sheets
| Generated Page | Template
| Auto System | ..\Infrastructure\Source\LightController\Generation\GenerateAutoSystem.xslt
Section | Generate DISCON Parameters
| Generated File | Template | Media | Encoding
| ..\Test\Parameters.xml | ..\Infrastructure\Source\LightController\Generation\GenerateParamsXml.xslt | xml | UTF-8
Section | Generate Documents
| Generated File | Template | Media | Encoding
| ..\Doc\LightController\Images\Images.html | ..\Infrastructure\Source\Main\Generation\GenerateStateMachinePicAll.xslt | html | UTF-8
| ..\Doc\LightController\IO.doc | ..\Infrastructure\Source\LightController\Generation\GenerateIODocumentation.xslt | html | UTF-8
| ..\Doc\LightController\A Parameters.doc | ..\Infrastructure\Source\Main\Generation\GenerateParametersDoc.xslt | html | UTF-8
| ..\Doc\LightController\B Calibrations.doc | ..\Infrastructure\Source\Main\Generation\GenerateCalibrationsDoc.xslt | html | UTF-8
| ..\Doc\LightController\C DerivedChannels.doc | ..\Infrastructure\Source\Main\Generation\GenerateDerivedChannelsDoc.xslt | html | UTF-8
| ..\Doc\LightController\D Alarms.doc | ..\Infrastructure\Source\Main\Generation\GenerateAlarmsDoc.xslt | html | UTF-8
| ..\Doc\LightController\E StateMachines.doc | ..\Infrastructure\Source\Main\Generation\GenerateStateMachineDoc.xslt | html | UTF-8
| ..\Doc\LightController\EmbedAllImages.bat | ..\Infrastructure\Source\Main\Generation\GenerateEmbedImages.xslt | html | UTF-8
Section | Generate Controller Source Code
| Generated File | Template | Media | Encoding
| .\LightController\Auto\TableDefs.h | ..\Infrastructure\Source\Main\Generation\GenerateTableDefsH.xslt | text | ISO-8859-1
| .\LightController\Auto\TableDefs.cc | ..\Infrastructure\Source\Main\Generation\GenerateTableDefsC.xslt | text | ISO-8859-1
| .\LightController\Auto\TableLookup.cc | ..\Infrastructure\Source\LightController\Generation\GenerateTableLookupC.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelAddresses.cc | ..\Infrastructure\Source\Main\Generation\GenerateChannelAddresses.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelAddresses.h | ..\Infrastructure\Source\Main\Generation\GenerateChannelAddressesH.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelBuffer.h | ..\Infrastructure\Source\Main\Generation\GenerateChannelBufferH.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelDefs.cc | ..\Infrastructure\Source\LightController\Generation\GenerateChannelsC.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelFuncs.h | ..\Infrastructure\Source\Main\Generation\GenerateGetSetFunctionsH.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelFuncs.cc | ..\Infrastructure\Source\Main\Generation\GenerateGetSetFunctions.xslt | text | ISO-8859-1
| .\LightController\Auto\ChannelAddressLookup.cc | ..\Infrastructure\Source\Platform\Win32\Generation\GenerateChannelAddressLookupC.xslt | text | ISO-8859-1
| .\LightController\Auto\DerivedChannels.cc | ..\Infrastructure\Source\Main\Generation\GenerateDerivedChannels.xslt | text | ISO-8859-1
| .\LightController\Auto\Calibration.cc | ..\Infrastructure\Source\Main\Generation\GenerateCalibration.xslt | text | ISO-8859-1
| .\LightController\Auto\AlarmLevels.h | ..\Infrastructure\Source\Main\Generation\GenerateAlarmLevels.xslt | text | ISO-8859-1
| .\LightController\Auto\InitialiseAlarms.cc | ..\Infrastructure\Source\Main\Generation\GenerateInitialiseAlarms.xslt | text | ISO-8859-1
| .\LightController\Auto\EvaluateAlarms.cc | ..\Infrastructure\Source\Main\Generation\GenerateEvaluateAlarms.xslt | text | ISO-8859-1
| .\LightController\Auto\StateMachine.h | ..\Infrastructure\Source\Main\Generation\GenerateStateMachineH.xslt | text | ISO-8859-1
| .\LightController\Auto\StateMachine.cc | ..\Infrastructure\Source\Main\Generation\GenerateStateMachineC.xslt | text | ISO-8859-1
| .\LightController\Auto\StateFilters.h | ..\Infrastructure\Source\Main\Generation\GenerateStateFiltersH.xslt | text | ISO-8859-1
| .\LightController\Auto\StateFilters.cc | ..\Infrastructure\Source\Main\Generation\GenerateStateFiltersC.xslt | text | ISO-8859-1
| .\LightController\Auto\ParamsXml.cc | ..\Infrastructure\Source\LightController\Generation\GenerateParamsXmlC.xslt | text | ISO-8859-1
| .\LightController\Discon\Discon.rc | ..\Infrastructure\Source\LightController\Generation\GenerateDllVersion.xslt | text | ISO-8859-1
| .\LightController\Auto\DisconIo.cc | ..\Infrastructure\Source\LightController\Generation\GenerateDisconIoC.xslt | text | ISO-8859-1
| .\LightController\Auto\DisconLogging.cc | ..\Infrastructure\Source\LightController\Generation\GenerateDisconLogging.xslt | text | ISO-8859-1
| ..\Test\LightController\BHTM\Dll.device | ..\Infrastructure\Test\Generation\GenerateDllDevice.xslt | xml | UTF-8
| ..\Test\LightController\BHTM\AlarmEnums.device | ..\Infrastructure\Test\Generation\GenerateAlarmEnumsDevice.xslt | xml | UTF-8
| ..\Test\LightController\BHTM\StateEnums.device | ..\Infrastructure\Test\Generation\GenerateStateEnumsDevice.xslt | xml | UTF-8
Section | Generate Installer
| Generated File | Template | Media | Encoding
| ..\Installer\Version.iss | ..\Infrastructure\Source\LightController\Generation\GenerateInstallerScript.xslt | text | ISO-8859-1
| ..\Installer\LightController\Installation Guide.doc | ..\Infrastructure\Source\LightController\Generation\GenerateInstallerGuide.xslt | html | UTF-8
Section | Output Directories
| Output Directory | Location
| Images | ..\Doc\LightController\Images
| Dotfiles | ..\Doc\LightController\Dotfiles
To generate code from this spreadsheet, run the batch file 'generate_light.bat' in the Source folder.
NOTE: It is important that the version information and Project Information sections come before other sections on this page.

## State Machine
;
Name | ;State Number | Subsystem | State Machine | Category | Exit Condition | Next State | Description en_GB | Display Name en_GB
;
PowerUp | 0 | Vspr | Vspr | PowerUp | NullPitchDemands(); | Action | Intialise pitch control outputs to null demands. | Power Up
PowerUp | 0 | Vspr | Vspr | PowerUp | true | WaitForStartupEnter
;
WaitForStartupEnter | 1 | Vspr | Vspr | WaitForStartup | S_SetStartupPowerFraction(0.0f); S_SetDisconnectedSpeedSetpointTarget(0.0f); D_SetDisconnectedSpeedSetpoint(0.0f); D_SetShaftPowerSetpointTargetRateLimited(0.0f); S_SetActiveMinimumPitchRate(0.0f); S_SetActiveMinimumPitchAngle( P_GetPositiveFeatherAngle() ); S_SetLvrtTorqueLimitTarget(P_GetMaximumGeneratorTorque()); | Action | Startup power setpoint is set to 0. Disconnected speed setpoint target is set to 0. Disconnected speed setpoint (rate limited) is set to 0. Shaft power setpoint (rate limited) is set to 0. De-rated speed setpoint is set to minimum between rated speed and speed setpoint input. Minimum pitch rate is set to 0. Minimum pitch angle is set to feather. LVRT torque limit is set to maximum generator torque. | Wait For Startup Enter
WaitForStartupEnter | 1 | Vspr | Vspr | WaitForStartup | true | WaitForStartup
WaitForStartup | 2 | Vspr | Vspr | WaitForStartup | D_SetDeRatedSpeed(std::max(0.0f, std::min(P_GetRatedGeneratorSpeed(), CI_GetAlgSpeedSetpointLimit()))); | Action | De-rated speed setpoint is set to minimum between rated speed and speed setpoint input. | Wait For Startup
WaitForStartup | 2 | Vspr | Vspr | WaitForStartup | CI_GetAlgStartupTurbine() | StartUpEnter | WaitForStartup state exited following startup request.
WaitForStartup | 2 | Vspr | Vspr | WaitForStartup | CI_GetAlgSpeedControlMode() | SpeedControlModeEnter | WaitForStartup state exited following manual startup request.
;
StartUpEnter | 3 | Vspr | Vspr | StartUp | S_SetShutdownFlag(false); EnableVspr(); | Action | The control algorithm enters VSPR mode. Shutdown flag is set to false and VSPR is enabled. | Start Up Enter
StartUpEnter | 3 | Vspr | Vspr | StartUp | true | StartUpWaitEnter
StartUpWaitEnter | 4 | Vspr | Vspr | StartUp | S_SetDisconnectedSpeedSetpointTarget(P_GetLowSpeedSyncSpeed()); S_SetActiveMinimumPitchRate(P_GetStartupMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(P_GetStartupWaitPitchangle()); D_SetRunUpPitchAngle2(P_GetStartupWaitPitchangle()); | Action
StartUpWaitEnter | 4 | Vspr | Vspr | StartUp | D_GetDurationStartUpWait() > P_GetStartupWaitTime() | StartUpSynchingSpeedEnter
StartUpSynchingSpeedEnter | 5 | Vspr | Vspr | StartUp | S_SetDisconnectedSpeedSetpointTarget(P_GetLowSpeedSyncSpeed()); S_SetStartPitchRate(P_GetRunupMinimumPitchRateLimit()); S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(std::max(D_GetRunUpPitchAngle1(), D_GetRunUpPitchAngle2())); | Action | Disconnected speed setpoint target is set to sync speed. Minimum pitch rate is set to minimum limit for startup. Regulate minimum pitch angle to a safe startup value. | Start Up Synching Speed Enter
StartUpSynchingSpeedEnter | 5 | Vspr | Vspr | StartUp | true | StartUpSynchingSpeed
StartUpSynchingSpeed | 6 | Vspr | Vspr | StartUp | S_SetStartPitchRate(P_GetRunupMinimumPitchRateLimit()); S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(std::max(D_GetRunUpPitchAngle1(), D_GetRunUpPitchAngle2())); | Action | Regulate minimum pitch angle to a safe startup value. | Start Up Synching Speed
StartUpSynchingSpeed | 6 | Vspr | Vspr | StartUp | D_GetDurationGeneratorSpeedWithinSyncTol() > P_GetGenSpeedAtSyncSpeedRequiredTime() | StartUpGeneratorConnection | State exited when generator speed has been within a set tolerance from synchronisation speed for the desired amount of time.
StartUpGeneratorConnection | 7 | Vspr | Vspr | StartUp | CO_SetAlgPcsSynchroniseRequest(true); S_SetStartPitchRate(P_GetRunupMinimumPitchRateLimit()); S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(std::max(D_GetRunUpPitchAngle1(), D_GetRunUpPitchAngle2())); | Action | Request converter synchronisation. Regulate minimum pitch angle to a safe startup value. | Start Up Generator Connection
StartUpGeneratorConnection | 7 | Vspr | Vspr | StartUp | CI_GetAlgPcsSynchronised() | StartUpConnectionLullEnter | State exited when converter is synchronised.
StartUpConnectionLullEnter | 8 | Vspr | Vspr | StartUp | S_SetStartPitchRate(P_GetRunupMinimumPitchRateLimit()); S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(D_GetRunUpPitchAngle2()); | Action | Minimum pitch angle is set to fine pitch. | Start Up Connection Lull Enter
StartUpConnectionLullEnter | 8 | Vspr | Vspr | StartUp | true | StartUpConnectionLull
StartUpConnectionLull | 9 | Vspr | Vspr | StartUp | S_SetStartPitchRate(P_GetPowerMinimumPitchRateLimit()); S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(D_GetRunUpPitchAngle2()); | Action | State exited after duration of connection lull. | Start Up Connection Lull
StartUpConnectionLull | 9 | Vspr | Vspr | StartUp | S_GetVsprStateCounter() > P_GetConnectionLullDuration() | StartUpPowerRampingEnter | State exited after duration of connection lull. | Start Up Connection Lull
StartUpPowerRampingEnter | 10 | Vspr | Vspr | StartUp | S_SetStartupPowerFraction(1.0f); | Action | Startup power setpoint is set to 100% of rated power. | Start Up Power Ramping Enter
StartUpPowerRampingEnter | 10 | Vspr | Vspr | StartUp | true | StartUpPowerRamping
StartUpPowerRamping | 11 | Vspr | Vspr | StartUp | S_SetStartPitchRate(P_GetPowerMinimumPitchRateLimit()); S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(D_GetRunUpPitchAngle2()); | Action | Power setpoint ramped towards target. State exited when the rate limited shaft power setpoint matches the target setpoint. | Start Up Power Ramping
StartUpPowerRamping | 11 | Vspr | Vspr | StartUp | D_GetShaftPowerSetpointTargetRateLimited() == D_GetShaftPowerSetpointTarget() | StartUpPowerRampingLullEnter | Power setpoint ramped towards target. State exited when the rate limited shaft power setpoint matches the target setpoint. | Start Up Power Ramping
StartUpPowerRampingLullEnter | 12 | Vspr | Vspr | StartUp | S_SetActiveMinimumPitchRate(P_GetMinimumPitchRateLimit()); S_SetActiveMinimumPitchAngle(P_GetMinimumFinePitch()); | Action | Minimum pitch rate is set to minimum limit for power production. | Start Up Power Ramping Lull Enter
StartUpPowerRampingLullEnter | 12 | Vspr | Vspr | StartUp | true | StartUpPowerRampingLull
StartUpPowerRampingLull | 13 | Vspr | Vspr | StartUp | S_GetVsprStateCounter() > P_GetPowerRampingLullDuration() | PowerProduction | State exited after duration of power ramping lull. | Start Up Power Ramping Lull
;
PowerProduction | 14 | Vspr | Vspr | PowerProduction | CI_GetAlgLowWindSpeed() | LowWindSpeedModeEnter | Power production state. Exit if Low Wind Speed Mode is activated. | Power Production
;
LowWindSpeedModeEnter | 15 | Vspr | Vspr | LowWindSpeedMode | D_SetShaftPowerSetpointTargetRateLimited (S_GetVsprQdem() * S_GetVsprFilteredSpeedTorque()); S_SetStartupPowerFraction(0.0f); | Action | The control algorithm enters low wind speed mode. Rate limited shaft power setpoint is set to current power demand. Startup power setpoint is set to 0% of rated power. | Low Wind Speed Mode Enter
LowWindSpeedModeEnter | 15 | Vspr | Vspr | LowWindSpeedMode | true | LowWindSpeedPowerRamping
LowWindSpeedPowerRamping | 16 | Vspr | Vspr | LowWindSpeedMode | D_GetShaftPowerSetpointTargetRateLimited() == D_GetShaftPowerSetpointTarget() | LowWindSpeedSynchingSpeed | Power setpoint ramped towards target. State exited when the rate limited shaft power setpoint matches the target setpoint. | Low Wind Speed Power Ramping
LowWindSpeedSynchingSpeed | 17 | Vspr | Vspr | LowWindSpeedMode | (CI_GetAlgRealPower() < P_GetShutdownMaxPower()) && (CI_GetAlgGeneratorSpeed() < (P_GetLowSpeedSyncSpeed() + P_GetSyncSpeedTol())) | LowWindSpeedGeneratorDisconnection | State exited when measured power is smaller than the shutdown power threshold and generator speed is within a set tolerance from synchronisation speed. | Low Wind Speed Synching Speed
LowWindSpeedGeneratorDisconnection | 18 | Vspr | Vspr | LowWindSpeedMode | CO_SetAlgPcsSynchroniseRequest(false); | Action | Request converter disconnection. | Low Wind Speed Generator Disconnection
LowWindSpeedGeneratorDisconnection | 18 | Vspr | Vspr | LowWindSpeedMode | !CI_GetAlgPcsSynchronised() | LowWindSpeedLull | State exited when converter is disconnected.
LowWindSpeedLull | 19 | Vspr | Vspr | LowWindSpeedMode | S_GetVsprStateCounter() > P_GetNormalShutdownLullDuration() | LowWindSpeedFreewheelingEnter | State exited after duration of disconnection lull. | Low Wind Speed Lull
LowWindSpeedFreewheelingEnter | 20 | Vspr | Vspr | LowWindSpeedMode | S_SetActiveMinimumPitchAngle(D_GetStartupPitchAngle()); S_SetDisconnectedSpeedSetpointTarget(P_GetLowWindSpeedGenSpeed()); | Action | Regulate minimum pitch angle to a safe startup value. Disconnected speed setpoint target is set to Low Wind Speed speed setpoint. | Low Wind Speed Freewheeling Enter
LowWindSpeedFreewheelingEnter | 20 | Vspr | Vspr | LowWindSpeedMode | true | LowWindSpeedFreewheeling
LowWindSpeedFreewheeling | 21 | Vspr | Vspr | LowWindSpeedMode | !CI_GetAlgLowWindSpeed() && S_GetVsprStateCounter() > P_GetLowWindSpeedModeMinDuration() | StartUpSynchingSpeedEnter | Freewheeling state. Exit if Low Wind Speed Mode is de-activated and the minimum time required in this state has passed. | Low Wind Speed Freewheeling
;
NormalShutdownEnter | 22 | Vspr | Vspr | NormalShutdown | S_SetShutdownFlag(true); S_SetShutdownMaxTorque(S_GetVsprQdem()); D_SetShaftPowerSetpointTargetRateLimited (S_GetVsprEnabled() ? S_GetVsprQdem() * S_GetVsprFilteredSpeedTorque() : 0); S_SetStartupPowerFraction(0.0f); | Action | The control algorithm enters a slow shutdown. Shutdown flag is set to false. Rate limited shaft power setpoint is set to current power demand (if VSPR is enabled) or to 0 (if VSPR is disabled). Startup power setpoint is set to 0% of rated power. | Slow Shutdown Enter
NormalShutdownEnter | 22 | Vspr | Vspr | NormalShutdown | !CI_GetAlgPcsSynchronised() | NormalShutdownGeneratorDisconnection | If converter is already disconnected exit to PitchToFeatherEnter state.
NormalShutdownEnter | 22 | Vspr | Vspr | NormalShutdown | true | NormalShutdownPowerRamping
NormalShutdownPowerRamping | 23 | Vspr | Vspr | NormalShutdown | D_GetShaftPowerSetpoint() < 10.0f | NormalShutdownSynchingSpeed | Power setpoint ramped towards target. State exited when the shaft power setpoint is very small. | Slow Shutdown Power Ramping
NormalShutdownSynchingSpeed | 24 | Vspr | Vspr | NormalShutdown | (CI_GetAlgRealPower() < P_GetShutdownMaxPower()) && (CI_GetAlgGeneratorSpeed() < (P_GetLowSpeedSyncSpeed() + P_GetSyncSpeedTol())) | NormalShutdownGeneratorDisconnection | State exited when measured power is smaller than the shutdown power threshold and generator speed is within a set tolerance from synchronisation speed. | Slow Shutdown Synching Speed
NormalShutdownGeneratorDisconnection | 25 | Vspr | Vspr | NormalShutdown | CO_SetAlgPcsSynchroniseRequest(false); CO_SetAlgPcsTorqueDemand(0.0f); | Action | Request converter disconnection. Maintain torque demand to 0. | Slow Shutdown Generator Disconnection
NormalShutdownGeneratorDisconnection | 25 | Vspr | Vspr | NormalShutdown | !CI_GetAlgPcsSynchronised() | NormalShutdownLull | State exited when converter is disconnected.
NormalShutdownLull | 26 | Vspr | Vspr | NormalShutdown | S_GetVsprStateCounter() > P_GetNormalShutdownLullDuration() | NormalShutdownPitchToFeatherEnter | State exited after duration of disconnection lull. | Slow Shutdown Lull
NormalShutdownPitchToFeatherEnter | 27 | Vspr | Vspr | NormalShutdown | DisableVspr(); ShutDownPitchDemand(D_GetNormalShutdownPitchRate()); | Action | Disable VSPR. Pitch all blades to feather at slow shutdown pitch rate. | Slow Shutdown Pitch To Feather Enter
NormalShutdownPitchToFeatherEnter | 27 | Vspr | Vspr | NormalShutdown | true | NormalShutdownPitchToFeather
NormalShutdownPitchToFeather | 28 | Vspr | Vspr | NormalShutdown | ShutDownPitchDemand(D_GetNormalShutdownPitchRate()); | Action | Pitch all blades to feather at slow shutdown pitch rate. | Slow Shutdown Pitch To Feather
NormalShutdownPitchToFeather | 28 | Vspr | Vspr | NormalShutdown | CI_GetAlgAllBladesAtFeather() | NormalShutdownComplete | State exited when all blades are at feather.
NormalShutdownComplete | 29 | Vspr | Vspr | NormalShutdown | NullPitchDemands(); | Action | Intialise pitch control outputs to null demands. | Slow Shutdown Complete
NormalShutdownComplete | 29 | Vspr | Vspr | NormalShutdown | true | WaitForStartupEnter
;
SpeedControlModeEnter | 30 | Vspr | Vspr | SpeedControlMode | S_SetShutdownFlag(false); EnableVspr(); S_SetActiveMinimumPitchRate(P_GetStartupMinimumPitchRateLimit()); | Action | The control algorithm enters Speed Control mode and begins turbine startup. | Speed Control Mode Enter
SpeedControlModeEnter | 30 | Vspr | Vspr | SpeedControlMode | true | SpeedControlMode
SpeedControlMode | 31 | Vspr | Vspr | SpeedControlMode | S_SetActiveMinimumPitchAngle( CI_GetAlgSpeedControlPitchLimit() ); S_SetDisconnectedSpeedSetpointTarget(CI_GetAlgSpeedControlSpeedSetpoint()); | Action | Speed Control state. Set minimum pitch angle and disconnected speed setpoint target to operator input values. | Speed Control Mode
;
AlgorithmResetEnter | 32 | Vspr | Vspr | AlgorithmReset | DisableVspr(); NullPitchDemands(); CO_SetAlgPcsSynchroniseRequest(false); CO_SetAlgPcsTorqueDemand(0.0f); | Action | The control algorithm enters Algorithm Reset mode. Disable VSPR. Intialise pitch control outputs to null demands. Request converter disconnection. Set torque demand to 0. | Algorithm Reset Enter
AlgorithmResetEnter | 32 | Vspr | Vspr | AlgorithmReset | true | AlgorithmReset
AlgorithmReset | 33 | Vspr | Vspr | AlgorithmReset | !CI_GetAlgAlgorithmReset() && !CI_GetAlgPcsSynchronised() && CI_GetAlgAllBladesAtFeather() | WaitForStartupEnter | Algorithm Reset state. State exited when all blades are at feather, converter is disconnected and algorithm reset shutdown request is reset | Algorithm Reset
;
VoltageDipEnter | 34 | Vspr | Vspr | Lvrt | S_SetLvrtOriginalMinPitchRate(S_GetActiveMinimumPitchRate()); S_SetActiveMinimumPitchRate(D_GetLvrtPitchKickRate()); S_SetLvrtTorqueLimitTarget(std::max(std::min(CI_GetAlgPcsVoltageDipTorqueLimit(), P_GetMaximumGeneratorTorque()),0.0f)); | Action | The control algorithm enters the Voltage Dip state. Store current minimum pitch rate value. Minimum pitch rate is set to LVRT pitch kick value. LVRT torque limit is set to minimum between maximum generator torque and torque limit from PCS. | Voltage Dip Enter
VoltageDipEnter | 34 | Vspr | Vspr | Lvrt | true | VoltageDipPitchKick
VoltageDipPitchKick | 35 | Vspr | Vspr | Lvrt | S_SetActiveMinimumPitchRate(D_GetLvrtPitchKickRate()); S_SetLvrtTorqueLimitTarget(std::max(std::min(CI_GetAlgPcsVoltageDipTorqueLimit(), P_GetMaximumGeneratorTorque()),0.0f)); | Action | Regulate minimum pitch rate to LVRT pitch kick value. LVRT torque limit is set to minimum between maximum generator torque and torque limit from PCS. | Voltage Dip Pitch Kick
VoltageDipPitchKick | 35 | Vspr | Vspr | Lvrt | S_GetVsprStateCounter() > P_GetLvrtPitchDuration() ¦¦ !CI_GetAlgPcsVoltageDip() | VoltageDipPitchKickComplete | State is exited when voltage dip is over or after duration of pitch kick.
VoltageDipPitchKickComplete | 36 | Vspr | Vspr | Lvrt | S_SetActiveMinimumPitchRate(S_GetLvrtOriginalMinPitchRate()); S_SetLvrtTorqueLimitTarget(std::max(std::min(CI_GetAlgPcsVoltageDipTorqueLimit(), P_GetMaximumGeneratorTorque()),0.0f)); | Action | Minimum pitch rate is set to original value. LVRT torque limit is set to minimum between maximum generator torque and torque limit from PCS. | Voltage Dip Pitch Kick Complete
VoltageDipPitchKickComplete | 36 | Vspr | Vspr | Lvrt | true | VoltageDip
VoltageDip | 37 | Vspr | Vspr | Lvrt | S_SetLvrtTorqueLimitTarget(std::max(std::min(CI_GetAlgPcsVoltageDipTorqueLimit(), P_GetMaximumGeneratorTorque()),0.0f)); | Action | LVRT torque limit is set to minimum between maximum generator torque and torque limit from PCS. | Voltage Dip
VoltageDip | 37 | Vspr | Vspr | Lvrt | !CI_GetAlgPcsVoltageDip() | VoltageDipRampTorqueLimit | State is exited when voltage dip is over.
VoltageDipRampTorqueLimit | 38 | Vspr | Vspr | Lvrt | S_SetLvrtTorqueLimitTarget(P_GetMaximumGeneratorTorque()); | Action | LVRT torque limit is set to maximum generator torque. | Voltage Dip Ramp Torque Limit
VoltageDipRampTorqueLimit | 38 | Vspr | Vspr | Lvrt | true | VoltageDipLull | Exit
VoltageDipLull | 39 | Vspr | Vspr | Lvrt | S_GetVsprStateCounter() > P_GetLvrtLullDuration() | StartUpPowerRampingEnter | State exited after duration of LVRT lull. | Voltage Dip Lull
;
GridLossShutdownEnter | 40 | Vspr | Vspr | GridLossShutdown | DisableVspr(); S_SetShutdownMaxTorque(CO_GetAlgPcsTorqueDemand()); | Action | The control algorithm enters the Grid Loss Shutdown state. Disable VSPR. Set maximum shutdown torque to current torque demand. | Grid Loss Shutdown Enter
GridLossShutdownEnter | 40 | Vspr | Vspr | GridLossShutdown | true | GridLossShutdownHoldTorque
GridLossShutdownHoldTorque | 41 | Vspr | Vspr | GridLossShutdown | ShutDownPitchDemand(D_GetGridLossShutdownPitchRate()); CO_SetAlgPcsTorqueDemand(D_GetGridLossShutdownTorque()); | Action | Pitch to feather at Grid Loss Shutdown pitch rate. Set torque demand to Grid Loss Shutdown torque value. | Grid Loss Shutdown Hold Torque
GridLossShutdownHoldTorque | 41 | Vspr | Vspr | GridLossShutdown | S_GetVsprStateCounter() > P_GetGridLossTorqueDuration() | GridLossShutdownCompletePitchRamp | State exited after duration of Grid Loss torque ramp.
GridLossShutdownCompletePitchRamp | 42 | Vspr | Vspr | GridLossShutdown | CO_SetAlgPcsSynchroniseRequest(false); CO_SetAlgPcsTorqueDemand(0.0f); ShutDownPitchDemand(D_GetGridLossShutdownPitchRate()); | Action | Pitch to feather at Grid Loss Shutdown pitch rate. | Grid Loss Shutdown Complete Pitch Ramp
GridLossShutdownCompletePitchRamp | 42 | Vspr | Vspr | GridLossShutdown | CI_GetAlgAllBladesAtFeather() | GridLossShutdownComplete | State exited when all blades are at feather.
GridLossShutdownComplete | 43 | Vspr | Vspr | GridLossShutdown | NullPitchDemands(); | Action | Intialise pitch control outputs to null demands. | Grid Loss Shutdown Complete
GridLossShutdownComplete | 43 | Vspr | Vspr | GridLossShutdown | true | WaitForStartupEnter
;
SlowShutdownEnter | 44 | Vspr | Vspr | SlowShutdown | DisableVspr(); D_SetFastShutdownTorque(CO_GetAlgPcsTorqueDemand()); | Action | The control algorithm enters the Normal Shutdown state. Disable VSPR. Set fast shutdown torque to current torque demand. | Normal Shutdown Enter
SlowShutdownEnter | 44 | Vspr | Vspr | SlowShutdown | true | SlowShutdownRampTorque
SlowShutdownRampTorque | 45 | Vspr | Vspr | SlowShutdown | ShutDownPitchDemand(P_GetSlowShutdownPitchRate()); CO_SetAlgPcsTorqueDemand(D_GetFastShutdownTorque()); | Action | Pitch to feather at Normal Shutdown pitch rate. Set torque demand to Fast Shutdown torque value. | Normal Shutdown Ramp Torque
SlowShutdownRampTorque | 45 | Vspr | Vspr | SlowShutdown | CI_GetAlgRealPower() <= P_GetShutdownMaxPower() | SlowShutdownCompletePitchRamp | State exited when measured power is smaller than the shutdown power threshold.
SlowShutdownCompletePitchRamp | 46 | Vspr | Vspr | SlowShutdown | CO_SetAlgPcsSynchroniseRequest(false); CO_SetAlgPcsTorqueDemand(0.0f); ShutDownPitchDemand(P_GetFastShutdownPitchRate()); | Action | Pitch to feather at Normal Shutdown pitch rate. | Normal Shutdown Complete Pitch Ramp
SlowShutdownCompletePitchRamp | 46 | Vspr | Vspr | SlowShutdown | !CI_GetAlgPcsSynchronised() && CI_GetAlgAllBladesAtFeather() | SlowShutdownComplete | State exited when all blades are at feather.
SlowShutdownComplete | 47 | Vspr | Vspr | SlowShutdown | NullPitchDemands(); | Action | Intialise pitch control outputs to null demands. | Normal Shutdown Complete
SlowShutdownComplete | 47 | Vspr | Vspr | SlowShutdown | true | WaitForStartupEnter
;
FastShutdownEnter | 48 | Vspr | Vspr | FastShutdown | DisableVspr(); D_SetFastShutdownTorque(CO_GetAlgPcsTorqueDemand()); FastShutdownPitchPositionDemand(); S_SetInitFastShutdown(true); | Action | The control algorithm enters the Fast Shutdown state. Disable VSPR. Set fast shutdown torque to current torque demand. | Fast Shutdown Enter
FastShutdownEnter | 48 | Vspr | Vspr | FastShutdown | true | FastShutdownRampTorque
FastShutdownRampTorque | 49 | Vspr | Vspr | FastShutdown | FastShutdownPitchPositionDemand(); CO_SetAlgPcsTorqueDemand(D_GetFastShutdownTorque()); | Action | Pitch to feather at Fast Shutdown pitch rate. Set torque demand to Fast Shutdown torque value. | Fast Shutdown Ramp Torque
FastShutdownRampTorque | 49 | Vspr | Vspr | FastShutdown | CI_GetAlgRealPower() <= P_GetShutdownMaxPower() | FastShutdownCompletePitchRamp | State exited when measured power is smaller than the shutdown power threshold.
FastShutdownCompletePitchRamp | 50 | Vspr | Vspr | FastShutdown | CO_SetAlgPcsSynchroniseRequest(false); CO_SetAlgPcsTorqueDemand(0.0f); FastShutdownPitchPositionDemand(); | Action | Pitch to feather at Fast Shutdown pitch rate. | Fast Shutdown Complete Pitch Ramp
FastShutdownCompletePitchRamp | 50 | Vspr | Vspr | FastShutdown | !CI_GetAlgPcsSynchronised() && CI_GetAlgAllBladesAtFeather() | FastShutdownComplete | State exited when all blades are at feather.
FastShutdownComplete | 51 | Vspr | Vspr | FastShutdown | NullPitchDemands(); | Action | Intialise pitch control outputs to null demands. | Fast Shutdown Complete
FastShutdownComplete | 51 | Vspr | Vspr | FastShutdown | true | WaitForStartupEnter
;
Universal |  | Vspr | Vspr | AlgorithmResetTransitions | CI_GetAlgAlgorithmReset() | AlgorithmResetEnter
Universal |  | Vspr | Vspr | NormalShutdownTransitions | CI_GetAlgNormalShutdown() | NormalShutdownEnter
Universal |  | Vspr | Vspr | VoltageDipTransitions | CI_GetAlgPcsVoltageDip() | VoltageDipEnter
Universal |  | Vspr | Vspr | GridLossShutdownTransitions | CI_GetAlgGridLossShutdown() | GridLossShutdownEnter
Universal |  | Vspr | Vspr | FastShutdownTransitions | CI_GetAlgFastShutdown() | FastShutdownEnter
Universal |  | Vspr | Vspr | SlowShutdownTransitions | CI_GetAlgSlowShutdown() | SlowShutdownEnter

## State Filter
;
Name | Subsystem | State Machine | Included Categories | Excluded Categories | Included States | Excluded States
;
StartUpStates | Vspr | Vspr | StartUp
NormalShutdownTransitions | Vspr | Vspr | * | AlgorithmReset, FastShutdown, GridLossShutdown, SlowShutdown, NormalShutdown
VoltageDipTransitions | Vspr | Vspr | PowerProduction |  | StartUpConnectionLullEnter, StartUpConnectionLull, StartUpPowerRampingEnter, StartUpPowerRamping, StartUpPowerRampingLullEnter, StartUpPowerRampingLull
GridLossShutdownTransitions | Vspr | Vspr | * | AlgorithmReset, GridLossShutdown
SlowShutdownTransitions | Vspr | Vspr | * | AlgorithmReset, FastShutdown, GridLossShutdown, SlowShutdown
FastShutdownTransitions | Vspr | Vspr | * | AlgorithmReset, GridLossShutdown, FastShutdown
AlgorithmResetTransitions | Vspr | Vspr | * | AlgorithmReset
PowerProductionStates | Vspr | Vspr | PowerProduction
ProducingStates | Vspr | Vspr | PowerProduction |  | StartUpConnectionLullEnter, StartUpConnectionLull, StartUpPowerRampingEnter, StartUpPowerRamping, StartUpPowerRampingLullEnter, StartUpPowerRampingLull, NormalShutdownEnter, NormalShutdownPowerRamping, NormalShutdownSynchingSpeed, NormalShutdownGeneratorDisconnection, LowWindSpeedModeEnter, LowWindSpeedPowerRamping, LowWindSpeedSynchingSpeed, LowWindSpeedGeneratorDisconnection
LowWindSpeedModeStates | Vspr | Vspr | LowWindSpeedMode
PitchFollowing | Vspr | Vspr | * | PowerUp, WaitForStartup, AlgorithmReset
NotInTorqueLossStates | Vspr | Vspr | * | GridLossShutdown, Lvrt
NotInVoltageDipStates | Vspr | Vspr | * | Lvrt

## Alarm
;
Name | ;Alarm Number | Subsystem | Description en_GB | Data Type | Initial Value | Alarm Level | Alarm Reset | Alarm Condition | State Filter | Reset Condition | Alarm Category | Display Name en_GB
;
; Algorithm Alarms
A_CutoutWindSpeed | 1 | Vspr | Triggered when the wind speed exceeds a defined threshold. | bool | false | RN | AT | D_GetCutoutWindSpeed1()>P_GetCutoutWindSpeed1() ¦¦ D_GetCutoutWindSpeed2()>P_GetCutoutWindSpeed2() | VsprNotInVoltageDipStates | C | Fault | Software Overspeed
A_SwOverSpeed | 1 | Vspr | Triggered when the measured generator speed exceeds a defined threshold. | bool | false | RF | AT | D_GetSwOverspeedDuration()> P_GetSwOverspeedMaxDuration() | VsprNotInVoltageDipStates | C | Fault | Software Overspeed
A_SustainedSwOverSpeed | 2 | Vspr | Triggered when the measured generator speed exceeds a defined threshold for longer than a specified amount of time. | bool | false | RF | AT | D_GetSustainedSwOverspeedDuration() > P_GetSustainedSwOverspeedMaxDuration() |  | C | Fault | Sustained Software Overspeed
A_LowPitchAngleOverspeed | 4 | Pitch | Triggered when the generator speed is above a defined limit and at the same time the mean pitch position demand of the three blades is below a defined threshold. | bool | false | RF | AT | CI_GetAlgGeneratorSpeed() > P_GetLowPitchAngleOverspeedSpeedLevel() && D_GetMeanPitchPositionDemand() < P_GetLowPitchAngleOverspeedPitchLevel() | VsprNotInVoltageDipStates | C | Fault | Low Pitch Angle Software Overspeed
A_NacelleAccelerationOverLimit | 5 | Vspr | Triggered when the nacelle acceleration effective value exceeds a defined threshold | bool | false | RF | AT | D_GetNacelleAccelerationEffectiveValue()>P_GetNacelleAccelerationLimit() | VsprNotInVoltageDipStates | C | Fault | Nacelle Acceleration Over Limit
A_PitchDemandSanityCheck | 6 | Pitch | Triggered when the generator is accelerating, the generator speed is above a defined limit and the rate of change of the collective pitch demand is less than a defined threshold. | bool | false | RF | AT | D_GetPitchDemandRate() < P_GetPitchSanityPitchRateLimit() && (P_GetPitchSanityDynamicActive()? CI_GetAlgGeneratorSpeed() > D_GetPowerControlSpeedSetpoint() :CI_GetAlgGeneratorSpeed() > P_GetPitchSanityGeneratorSpeedLevel() )&& D_GetEstimatedGeneratorAcceleration() > 0.0f | VsprNotInVoltageDipStates | C | Fault | Pitch Demand Sanity Check
A_CollectivePitchRateToFine | 7 | Pitch | Triggered when the rate of change of the collective pitch demand is less than a defined limit (usually set slightly lower than the software limit). | bool | false | RF | AT | D_GetPitchDemandRate() < P_GetCollectivePitchMinRate() |  | C | Fault | Collective pitch rate too fast towards fine pitch
A_CollectivePitchAngleBelowFine | 8 | Pitch | Triggered when the mean pitch position demand of the three blades is less than a defined limit (usually set slightly lower than the software limit). | bool | false | RF | AT | D_GetMeanPitchPositionDemand()<P_GetCollectivePitchMinAngle() |  | C | Fault | Collective pitch angle demand below fine pitch angle
A_CollectivePitchBelowScheduledFine | 9 | Pitch | Triggered when the mean measured pitch position of the three blades is lower than a defined limit (usually set slightly lower than the minimum pitch angle at rated power) and the demanded power is above a defined threshold. | bool | false | RF | AT | D_GetCurrentMeasuredPitchAngle123()<P_GetCollectivePitchMinAngleForRated() && S_GetVsprQdem() * S_GetVsprFilteredSpeedTorque() > P_GetPowerForCollectivePitchMinAngle() |  | C | Fault | Collective pitch below schedule fine pitch angle
A_PitchDemandDifferenceError12 | 10 | Pitch | Triggered when the difference between the pitch position demands of Blade 1 and Blade 2 exceeds a defined limit. | bool | false | RF | AT | D_GetPitchDemandDifference12() > P_GetMaxPitchDemandDifference() |  | C | Fault | Pitch Demand Difference Error 12
A_PitchDemandDifferenceError23 | 11 | Pitch | Triggered when the difference between the pitch position demands of Blade 2 and Blade 3 exceeds a defined limit. | bool | false | RF | AT | D_GetPitchDemandDifference23() > P_GetMaxPitchDemandDifference() |  | C | Fault | Pitch Demand Difference Error 23
A_PitchDemandDifferenceError13 | 12 | Pitch | Triggered when the difference between the pitch position demands of Blade 1 and Blade 3 exceeds a defined limit. | bool | false | RF | AT | D_GetPitchDemandDifference13() > P_GetMaxPitchDemandDifference() |  | C | Fault | Pitch Demand Difference Error 13
A_PitchPositonDifferenceError12 | 13 | Pitch | Triggered when the difference between the measured pitch positionof Blade 1 and Blade 2 exceeds a defined limit. | bool | false | RP | AT | D_GetPitchPositionDifference12() > P_GetMaxPitchPositionDifference() |  | C | Fault | Pitch Demand Difference Error 12
A_PitchPositionDifferenceError23 | 14 | Pitch | Triggered when the difference between the measured pitch positionof Blade 2 and Blade 3 exceeds a defined limit. | bool | false | RP | AT | D_GetPitchPositionDifference23() > P_GetMaxPitchPositionDifference() |  | C | Fault | Pitch Demand Difference Error 23
A_PitchPositionDifferenceError13 | 15 | Pitch | Triggered when the difference between the measured pitch positionof Blade 1 and Blade 3 exceeds a defined limit. | bool | false | RP | AT | D_GetPitchPositionDifference13() > P_GetMaxPitchPositionDifference() |  | C | Fault | Pitch Demand Difference Error 13
A_PitchFollowingError1 | 16 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 1 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RP | AT | !CI_GetSafetySystemTrigger() && D_GetFollowingErrorDuration1() > P_GetPitchFollowingErrorMaxDuration() | VsprPitchFollowing | C | Fault | Pitch Following Error 1
A_PitchFollowingError2 | 17 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 2 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RP | AT | !CI_GetSafetySystemTrigger() && D_GetFollowingErrorDuration2() > P_GetPitchFollowingErrorMaxDuration() | VsprPitchFollowing | C | Fault | Pitch Following Error 2
A_PitchFollowingError3 | 18 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 3 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RP | AT | !CI_GetSafetySystemTrigger() && D_GetFollowingErrorDuration3() > P_GetPitchFollowingErrorMaxDuration() | VsprPitchFollowing | C | Fault | Pitch Following Error 3
;A_PitchFollowingErrorRate1 | 19 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 1 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RP | AT | D_GetFollowingErrorRateDuration1() > P_GetPitchFollowingErrorMaxDuration() | VsprPitchFollowing | C | Fault | Pitch Following Error Rate 1
;A_PitchFollowingErrorRate2 | 20 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 2 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RP | AT | D_GetFollowingErrorRateDuration2() > P_GetPitchFollowingErrorMaxDuration() | VsprPitchFollowing | C | Fault | Pitch Following Error Rate 2
;A_PitchFollowingErrorRate3 | 21 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 3 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RP | AT | D_GetFollowingErrorRateDuration3() > P_GetPitchFollowingErrorMaxDuration() | VsprPitchFollowing | C | Fault | Pitch Following Error Rate 3
A_PitchFollowingErrorVspr1 | 22 | Pitch | Triggered when, during normal power production, the difference between the measured pitch position and an estimate of the pitch position (based on a model of the actuator) of Blade 1 exceeds a defined limit. | bool | false | RP | AT | !CI_GetSafetySystemTrigger() && (float) fabs(S_GetExpectedPitchAngle1() - CI_GetAlgPitchPosition1()) > P_GetMaximumPitchFollowingErrorVspr() && S_GetVsprEnabled()&&(CI_GetAlgPitchPosition1()<P_GetStartupWaitPitchangle() ) | VsprNotInVoltageDipStates | C | Fault | Pitch Following Error Vspr 1
A_PitchFollowingErrorVspr2 | 23 | Pitch | Triggered when, during normal power production, the difference between the measured pitch position and an estimate of the pitch position (based on a model of the actuator) of Blade 2 exceeds a defined limit. | bool | false | RP | AT | !CI_GetSafetySystemTrigger() && (float) fabs(S_GetExpectedPitchAngle2() - CI_GetAlgPitchPosition2()) > P_GetMaximumPitchFollowingErrorVspr() && S_GetVsprEnabled()&&(CI_GetAlgPitchPosition2()<P_GetStartupWaitPitchangle() ) | VsprNotInVoltageDipStates | C | Fault | Pitch Following Error Vspr 2
A_PitchFollowingErrorVspr3 | 24 | Pitch | Triggered when, during normal power production, the difference between the measured pitch position and an estimate of the pitch position (based on a model of the actuator) of Blade 3 exceeds a defined limit. | bool | false | RP | AT | !CI_GetSafetySystemTrigger() && (float) fabs(S_GetExpectedPitchAngle3() - CI_GetAlgPitchPosition3()) > P_GetMaximumPitchFollowingErrorVspr() && S_GetVsprEnabled()&&(CI_GetAlgPitchPosition3()<P_GetStartupWaitPitchangle() ) | VsprNotInVoltageDipStates | C | Fault | Pitch Following Error Vspr 3
A_HighYawError | 25 | Yaw | Triggered when a 3s moving average of the measured yaw misalignment exceeds a defined limit, scheduled against a 300s moving average of the measured wind speed | bool | false | RN | AT | S_GetYawDeratingStopMode() |  | C | Normal | Instantaneous High Yaw Error
A_NonLinearPitchActionTriggered | 26 | Pitch | Trigered when a non-linear pitch action is triggered | bool | false | RW | AT | D_GetNonLinearPitchActionTriggered() |  | C | Warning | Non Linear Pitch rate triggered
A_IPCDemandErrorVspr | 27 | Vspr | Triggered when the difference between the average demand of the three blades and the collective pitch demand exceeds a defined limit. | bool | false | RF | AT | (float) fabs(D_GetIpcDemandError()) > P_GetMaxIpcDemandError() | VsprProducingStates | C | Fault | IPC demand Error
A_LowPitchAngle1 | 28 | Pitch | Triggered when demanded pitch angle of Blade 1 is below a specified threshold | bool | false | RF | AT | CO_GetAlgPitchPositionDemand1() < P_GetMinIndivPitchAngle() |  | C | Fault | Pitch Following Error 1
A_LowPitchAngle2 | 29 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 2 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RF | AT | CO_GetAlgPitchPositionDemand2() < P_GetMinIndivPitchAngle() |  | C | Fault | Pitch Following Error 2
A_LowPitchAngle3 | 30 | Pitch | Triggered when the difference between the pitch position demand and the measured pitch position of Blade 3 exceeds a defined limit for longer than a defined time. Only active when the collective pitch demand is below a defined threshold. | bool | false | RF | AT | CO_GetAlgPitchPositionDemand3() < P_GetMinIndivPitchAngle() |  | C | Fault | Pitch Following Error 3
;
; Timing performance checks
A_ExecutionTimeOverrun | 31 | Monitor | Triggered when there is a serious overrun of the controller core code execution | bool | false | RET | AT | S_GetTimingMonitoringAlarmsEnabled() && (S_GetTimeForAll() > P_GetExecutionTimeOverrunThreshold()) |  | C | Fault | Controller Execution Time Overrun
A_ShortAverageCycleTimeMismatch | 32 | Monitor | Triggered when the short-averaged measured controller cycle time diverges steadily from the expected value | bool | false | RET | AT | S_GetTimingMonitoringAlarmsEnabled() && (fabs(D_GetShortAverageMeasuredCycleTime() - P_GetControllerCycleTime()) > P_GetShortAvgCycleTimeMismatchFactor()*P_GetControllerCycleTime()) |  | C | Fault | Short Average Measured Controller Cycle Time Mismatch
A_LongAverageCycleTimeMismatch | 33 | Monitor | Triggered when the long-averaged measured controller cycle time diverges steadily from the expected value | bool | false | RET | AT | S_GetTimingMonitoringAlarmsEnabled() && (fabs(D_GetLongAverageMeasuredCycleTime() - P_GetControllerCycleTime()) > P_GetLongAvgCycleTimeMismatchFactor()*P_GetControllerCycleTime()) |  | C | Fault | Long Average Measured Controller Cycle Time Mismatch
A_LidarError | 35 | Vspr | Trggered when the Lidar error | bool | false | RN | AT | (D_GetLidarMeasureWindFaultDuration()>P_GetLidarV0LErrorTimeThreshold())&&S_GetFaultNumber() |  | C | Fault | Lidar Error
;

## Auto System
;
Name | Data Type | Initial Value | Subsystem | Expression | Filter Type | Discon Log | Descriptionen_ G B | Visibility
;
D_Warning | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_WARNING | PosEdge |  | Highest alarm has just (raising edge) changed to Warning level | Public
D_WarningActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_WARNING |  |  | Highest alarm level is Warning | Public
D_NormalShutdown | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_NORMAL_SHUTDOWN | PosEdge |  | Highest alarm has just (raising edge) changed to NormalShutdown level | Public
D_NormalShutdownActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_NORMAL_SHUTDOWN |  |  | Highest alarm level is NormalShutdown | Public
D_SlowShutdown | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_SLOW_SHUTDOWN | PosEdge |  | Highest alarm has just (raising edge) changed to SlowShutdown level | Public
D_SlowShutdownActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_SLOW_SHUTDOWN |  |  | Highest alarm level is SlowShutdown | Public
D_GridLossShutdown | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_GRID_LOSS_SHUTDOWN | PosEdge |  | Highest alarm has just (raising edge) changed to GridLossShutdown level | Public
D_GridLossShutdownActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_GRID_LOSS_SHUTDOWN |  |  | Highest alarm level is GridLossShutdown | Public
D_FastShutdown | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_FAST_SHUTDOWN | PosEdge |  | Highest alarm has just (raising edge) changed to FastShutdown level | Public
D_FastShutdownActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_FAST_SHUTDOWN |  |  | Highest alarm level is FastShutdown | Public
D_PitchBatteryShutdown | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_PITCH_BATTERY_SHUTDOWN | PosEdge |  | Highest alarm has just (raising edge) changed to PitchBatteryShutdown level | Public
D_PitchBatteryShutdownActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_PITCH_BATTERY_SHUTDOWN |  |  | Highest alarm level is PitchBatteryShutdown | Public
D_SafetyTurbineShutdown | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_SAFETY_TURBINE_SHUTDOWN | PosEdge |  | Highest alarm has just (raising edge) changed to SafetyTurbineShutdown level | Public
D_SafetyTurbineShutdownActive | bool | false | Controller | S_GetHighestActiveAlarm() == RESPONSE_SAFETY_TURBINE_SHUTDOWN |  |  | Highest alarm level is SafetyTurbineShutdown | Public
S_HighestActiveAlarm | int | 0 | Controller |  |  | true | The highest alarm level (Enumerated type) | Public
S_HighestActiveAlarmId | int | 0 | Controller |  |  | true | The id of one of the alarm at the highest alarm level | Public
S_VsprState | int | 0 | Vspr |  |  | true | The current state of the Vspr state machine | Public
S_VsprStateCounter | float | 0 | Vspr |  |  |  | The amount of time (seconds) the Vspr state machine is in current state | Public

## CIO
; | [6 empty] | Sensor Requirements |  | Calibrations |  |  | Bladed |  | HMI
Name | Subsystem | Description en_GB | Data Type | Initial Value | Calibration Category | Units | Nom Sample Rate Hz | Requirements | Calibration Expression | Full Controller Calibration Expression | Reset Condition | Discon Log | Dimensions | Display Name en_GB | Display Location en_GB | Display Units | Logging Config
;
; Supervisory
CI_AlgSpeedControlMode | Vspr | Enter speed control mode | bool | false | Sim DIO |  |  |  |  | InControllerSpeedControlAlgorithmEnabledStatesFilter() | W |  |  | Speed Control Mode | IO.Algorithm.Supervisory
CI_AlgSpeedControlSpeedSetpoint | Vspr | Speed setpoint for speed control mode | float | 0 | Sim MiscIn | rad/s |  |  |  | UC_GetSpeedControlGeneratorSpeedSetpoint() | W |  | A/T | Speed Control Setpoint | IO.Algorithm.Supervisory
CI_AlgSpeedControlPitchLimit | Vspr | Minimum allowed pitch for speed control mode | float | 0 | Sim MiscIn | rad |  |  |  | UC_GetSpeedControlMinimumPitchAngle() | W |  | A | Speed Control Pitch Limit | IO.Algorithm.Supervisory
CI_AlgStartupTurbine | Vspr | Trigger a turbine startup | bool | false | DIO |  |  |  |  | bespoke | W | true |  | Startup Turbine | IO.Algorithm.Supervisory
CI_AlgLowWindSpeed | Vspr | Trigger the Low Wind Speed operating mode | bool | false | DIO |  |  |  |  | bespoke | W |  |  | Low Wind Speed | IO.Algorithm.Supervisory
CI_AlgNormalShutdown | Vspr | Trigger a normal shutdown | bool | false | DIO |  |  |  |  | bespoke | W | true |  | Normal Shutdown | IO.Algorithm.Supervisory
CI_AlgAlgorithmReset | Vspr | Reset Algorithm State Machine (used for external shutdowns) | bool | false | DIO |  |  |  |  | bespoke | W | true |  | Algorithm Reset | IO.Algorithm.Supervisory
CI_SafetySystemTrigger | Vspr | CI_SafetySystemTrigger | bool | false | DIO
CI_AlgPcsVoltageDip | Vspr | Voltage dip indicator | bool | false | Sim DIO |  |  |  |  | CI_GetPcsLvrt() | W | false |  | PCS Voltage Dip | IO.Algorithm.Supervisory
CI_AlgPcsVoltageDipTorqueLimit | Vspr | Maximum torque provided by PCS during LVRT | float | 0 | DIO | Nm |  |  |  |  | W | false | FL | PCS Voltage Dip Torque Limit | IO.Algorithm.Supervisory
CI_AlgGridLossShutdown | Vspr | Grid loss indicator | bool | false | DIO |  |  |  |  | bespoke | W | true |  | Grid Loss Shutdown | IO.Algorithm.Supervisory
CI_AlgSlowShutdown | Vspr | Trigger a slow shutdown | bool | false | DIO |  |  |  |  | bespoke | W | true |  | Slow shutdown | IO.Algorithm.Supervisory
CI_AlgFastShutdown | Vspr | Trigger a fast shutdown | bool | false | DIO |  |  |  |  | bespoke | W | true |  | Fast Shutdown | IO.Algorithm.Supervisory
CI_AlgPowerSetpointLimit | Vspr | Maximum power setpoint in power production | float | 0 | Sim MiscIn | W |  |  |  | D_GetTurbinePowerSetpointForVspr() | W | true | P | Power Setpoint Limit | IO.Algorithm.Supervisory | kW
CI_AlgSpeedSetpointLimit | Vspr | Maximum speed setpoint in power production | float | 0 | Sim MiscIn | rad/s |  |  |  | D_GetGeneratorSpeedSetpointForVspr() | W |  | A/T | Speed Setpoint Limit | IO.Algorithm.Supervisory | rpm
CO_AlgNormalShutdown | Vspr | The control algorithm has detected an alarm requiring a normal shutdown. | bool | false | DIO Supervisory |  |  |  | D_GetNormalShutdown() |  | W
CO_AlgGridLossShutdown | Vspr | The control algorithm has detected an alarm requiring a grid loss shutdown. | bool | false | DIO Supervisory |  |  |  | D_GetGridLossShutdown() |  | W
CO_AlgSlowShutdown | Vspr | The control algorithm has detected an alarm requiring a fast shutdown. | bool | false | DIO Supervisory |  |  |  | D_GetSlowShutdown() |  | W
CO_AlgFastShutdown | Vspr | The control algorithm has detected an alarm requiring a fast shutdown. | bool | false | DIO Supervisory |  |  |  | D_GetFastShutdown() |  | W | true
CO_AlgAutonomousFeather | Vspr | The control algorithm has detected an alarm requiring an autonomous feather. | bool | false | DIO Supervisory |  |  |  | D_GetPitchBatteryShutdown() |  | W
CO_AlgWaitForStartup | Vspr | The control algorithm is waiting for turbine startip trigger | bool | false | Sim DIO Supervisory |  |  |  | S_GetVsprState() == VsprWaitForStartup | S_GetVsprState() == VsprWaitForStartup | W |  |  | Wait For Startup | IO.Algorithm.Supervisory
CO_AlgInPowerProduction | Vspr | The control algorithm is in power production full power mode | bool | false | DIO Supervisory |  |  |  | S_GetVsprState() == VsprPowerProduction | S_GetVsprState() == VsprPowerProduction | W |  |  | Power Production | IO.Algorithm.Supervisory
CO_AlgInLowWindSpeedMode | Vspr | The control algorithm is in low wind speed mode | bool | false | DIO Supervisory |  |  |  | InVsprLowWindSpeedModeStatesFilter() | InVsprLowWindSpeedModeStatesFilter() | W |  |  | Low Wind Speed | IO.Algorithm.Supervisory
CO_AlgInSpeedControlMode | Vspr | The control algorithm is in speed control mode | bool | false | DIO Supervisory |  |  |  | S_GetVsprState() == VsprSpeedControlMode | S_GetVsprState() == VsprSpeedControlMode | W |  |  | Speed Control | IO.Algorithm.Supervisory
CI_AlgWatchdog | Vspr | A watchdog input from the control system. This is not monitored for failures, but is repeated on CO_Watchdog to detect control algorithm failures. | bool | false | MiscIn | [5 empty] | W
CO_AlgWatchdog | Vspr | A watchdog output from the control algorithm - echos the value of CI_Watchdog. | bool | false | Sim MiscIn |  |  |  | CI_GetAlgWatchdog() | CO_GetControllerWatchdog() | W |  |  | Watchdog | IO.Algorithm.Supervisory
;
; Turbine Measurements
CI_AlgRotorAzimuth | Vspr | Measured rotor azimuth | float | 0 | Sim MiscIn | deg | 50 |  |  | CI_GetRotorPosition() | W | true | A | Rotor Azimuth | IO.Algorithm.TurbMeas | deg
CI_AlgAverageWindSpeed | Anem | 1s averaged wind speed | float | 0 | Sim MiscIn | m/s | 1 | Accuracy of 1m/s at turbine cut-in wind speed, 1m/s at turbine cut-out wind speed |  |  | W | true | L/T | Short Term Avg Wind Speed | IO.Algorithm.TurbMeas | m/s
CI_AlgYawError | Yaw | Measured yaw error | float | 0 | Sim Yaw | rad | 1 | Accuracy of 5deg within the power production wind speed range |  | CI_GetMeasuredYawError() | W | true | A | Yaw Error | IO.Algorithm.TurbMeas | deg
;
; Pcs Interface
CI_AlgPcsSynchronised | Pcs | Indicator that the PCS is synchronised to the grid | bool | false | Sim Pcs |  |  |  |  | CO_GetPcsState() == PCS_STATE_GENERATING | W | true |  | PCS Synchronised | IO.Algorithm.PCS
CI_AlgElectricalTorque | Pcs | Measured torque | float | 0 | Sim Pcs | N.m | 50 | 10s avg to 2% of rated |  | CI_GetPcsMeasuredElectricalTorque() | W |  | FL | Electrical Torque | IO.Algorithm.PCS | kN.m
CI_AlgGeneratorSpeed | Pcs | Measured generator speed | float | 0 | Sim Pcs | rad/s | 50 | Repeatability better than +/-0.025% over the power production and overspeed range. Repeatability better than +/-0.1% at lower speeds. Accuracy of 0.1% ofnominal speed, averaged over 1s. Total latency to GH control algorithm <= 40ms. |  | (CO_GetPcsState() == PCS_STATE_GENERATING) ? CI_GetPcsMeasuredGeneratorSpeed() : CI_GetGeneratorSpeed() | W | true | A/T | Generator Speed | IO.Algorithm.PCS | rpm
CI_AlgShaftPower | Pcs | Shaft power | float | 0 | Sim Pcs | W | 10 | Repeatability better than +/-1%. Accuracy better than +/-2%. Total latency to GH control algorithm <= 200ms. |  | CI_GetShaftPower() | W |  | P | Shaft Power | IO.Algorithm.PCS | kW
CI_AlgRealPower | Pcs | Measured electrical power | float | 0 | Sim Pcs | W | 10 | Repeatability better than +/-1%. Accuracy better than +/-2%. Total latency to GH control algorithm <= 200ms. |  | CI_GetPcsActivePower() | W | true | P | Real Power | IO.Algorithm.PCS | kW
CO_AlgPcsSynchroniseRequest | Pcs | Request PCS synchronisation to the grid | bool | false | Sim Pcs |  | 50 |  |  | bespoke | W | true |  | PCS Synchronise Request | IO.Algorithm.PCS
CO_AlgPcsTorqueDemand | Pcs | Control algorithm demanded generator torque | float | 0 | Sim Pcs | N.m | 50 |  |  | bespoke | W | true | FL | PCS Torque Demand | IO.Algorithm.PCS | kN.m
;
; Pitch Interface
CI_AlgMinimumPitchAngle | Pitch | Minimum pitch angle (used to implement pitch greasing in power production) | float | -0.01745 | Sim Pitch | rad |  |  |  | P_GetMinimumFinePitch() | W | true | A | Minimum Pitch Angle | IO.Algorithm.Pitch | deg
CI_AlgAllBladesAtFeather | Pitch | All blades at feather | bool | false | Sim Pitch |  |  |  |  | CI_GetPitchAllBladesAtFeather() | W | true |  | All Blades At Feather | IO.Algorithm.Pitch
CI_AlgPitchPosition1 | Pitch | Blade 1 Pitch Position | float | 0 | Sim Pitch | rad | 25 | Accuracy of 0.1 degree. Total latency to GH control algorithm <= 80ms. |  | CI_GetPitchPosition1() | C | true | A | Pitch Position 1 | IO.Algorithm.Pitch | deg
CI_AlgPitchPosition2 | Pitch | Blade 2 Pitch Position | float | 0 | Sim Pitch | rad | 25 | Accuracy of 0.1 degree. Total latency to GH control algorithm <= 80ms. |  | CI_GetPitchPosition2() | C | true | A | Pitch Position 2 | IO.Algorithm.Pitch | deg
CI_AlgPitchPosition3 | Pitch | Blade 3 Pitch Position | float | 0 | Sim Pitch | rad | 25 | Accuracy of 0.1 degree. Total latency to GH control algorithm <= 80ms. |  | CI_GetPitchPosition3() | C | true | A | Pitch Position 3 | IO.Algorithm.Pitch | deg
CO_AlgPitchPositionDemand1 | Pitch | Blade 1 Pitch Position Demand | float | 0 | Pitch | rad | 25 |  |  | bespoke | C | true | A | Pitch Position Demand 1 | IO.Algorithm.Pitch | deg
CO_AlgPitchPositionDemand2 | Pitch | Blade 2 Pitch Position Demand | float | 0 | Pitch | rad | 25 |  |  | bespoke | C | true | A | Pitch Position Demand 2 | IO.Algorithm.Pitch | deg
CO_AlgPitchPositionDemand3 | Pitch | Blade 3 Pitch Position Demand | float | 0 | Pitch | rad | 25 |  |  | bespoke | C | true | A | Pitch Position Demand 3 | IO.Algorithm.Pitch | deg
CO_AlgPitchRateDemand1 | Pitch | Blade 1 Pitch Rate Demand | float | 0 | Pitch | rad/s | 100 |  |  | bespoke | C | true | A/T | Pitch Rate Demand 1 | IO.Algorithm.Pitch | deg/s
CO_AlgPitchRateDemand2 | Pitch | Blade 2 Pitch Rate Demand | float | 0 | Pitch | rad/s | 100 |  |  | bespoke | C | true | A/T | Pitch Rate Demand 2 | IO.Algorithm.Pitch | deg/s
CO_AlgPitchRateDemand3 | Pitch | Blade 3 Pitch Rate Demand | float | 0 | Pitch | rad/s | 100 |  |  | bespoke | C | true | A/T | Pitch Rate Demand 3 | IO.Algorithm.Pitch | deg/s
;
; Acceleration interface
CI_AlgNacelleForeAftAcceleration | Vib | Nacelle Fore-aft acceleration | float | 0 | Sim Vib | m/s/s | 12.5 | Repeatability better than 0.005 m/s^2. Accuracy of 0.05 m/s^s between 0.1Hz to 10Hz. Total latency to GH control algorithm <= 80ms. |  | CI_GetVibNacelleForeAftAcceleration() | W |  | L/TT | Nacelle Fore Aft Acceleration | IO.Algorithm.Accel | m/s/s
CI_AlgNacelleSideSideAcceleration | Vib | Nacelle side-side acceleration | float | 0 | Sim Vib | m/s/s | 12.5 | Repeatability better than 0.005 m/s^2. Accuracy of 0.05 m/s^s between 0.1Hz to 10Hz. Total latency to GH control algorithm <= 80ms. |  | CI_GetVibNacelleSideSideAcceleration() | W |  | L/TT | Nacelle Side Side Acceleration | IO.Algorithm.Accel | m/s/s
;
; Blade Loads
CI_AlgBladeLoadsOk | Loads | Condition of blade loads measurement | bool | false | Loads | [5 empty] | W | true |  | Blade Loads Ok | IO.Algorithm.Loads
CI_AlgOutOfPlaneBendingMoment1 | Loads | Blade 1 out-of-plane bending moment | float | 0 | Loads | Nm | 100 |  |  |  | W | true | FL | Out-of-Plane Bending Moment 1 | IO.Algorithm.Loads | N.m
CI_AlgOutOfPlaneBendingMoment2 | Loads | Blade 2 out-of-plane bending moment | float | 0 | Loads | Nm | 100 |  |  |  | W | true | FL | Out-of-Plane Bending Moment 2 | IO.Algorithm.Loads | N.m
CI_AlgOutOfPlaneBendingMoment3 | Loads | Blade 3 out-of-plane bending moment | float | 0 | Loads | Nm | 100 |  |  |  | W | true | FL | Out-of-Plane Bending Moment 3 | IO.Algorithm.Loads | N.m
;
; Blade clearance
CI_MeasuredBlade1StationPositionX | Vspr | Blade1StationPositionX | float | 0 | Vspr | m | 50 |  |  |  |  | true | L
CI_MeasuredBlade2StationPositionX | Vspr | Blade2StationPositionX | float | 0 | Vspr | m | 50 |  |  |  |  | true | L
CI_MeasuredBlade3StationPositionX | Vspr | Blade3StationPositionX | float | 0 | Vspr | m | 50 |  |  |  |  | true | L
;功率曲线准许生成标志位
CI_GenPowerCurveEn | Vspr | 主控功率曲线准许生成标志位-影响MFPI功能 | bool | true | DIO | [5 empty] | W
CO_GenPowerCurveEn | Vspr | 控制策略功率曲线准许生成标志位 | bool | false | DIO |  |  |  | !(S_GetYawDeratingFlag()¦¦S_GetNacAccXDeratingFlag()¦¦S_GetTurDeratingFlag()¦¦S_GetHighWindDeratingFlag()) |  | W

## State
; | [8 empty] | HMI
Name | Subsystem | Description en_GB | Data Type | Initial Value | Reset Condition | Interface Log | Discon Log | Dimensions | Display Name en_GB | Display Location en_GB | Display Units | Logging Config
;Overall execution timing monitoring
S_TimingMonitoringAlarmsEnabled | Monitor | Flag to enable and disable timing monitoring alarms | bool | true | W |  |  |  | Timing Monitoring Alarms Enabled | IO.State.Perf
S_MeasuredControllerCycleTime | Monitor | Milliseconds between consecutive calls to execute the controller code | float | 0 | W |  |  | T | Measured Controller Cycle Time | IO.State.Perf | ms
S_TimeForAll | Monitor | Milliseconds taken by one execution of all controller code (read + step + write) | float | 0 | W |  |  | T | Time For All | IO.State.Perf | ms
S_TimeForStepController | Monitor | Time For Step Controller (All except Read/Write Channels Interface) | float | 0 | W |  |  | T | Time For StepController | IO.State.Perf | ms
S_TimeForReadChannelsInterface | Monitor | Time For Read Channels Interface | float | 0 | W |  |  | T | Time For ReadChannelsInterface | IO.State.Perf | ms
S_TimeForWriteChannelsInterface | Monitor | Time For Write Channels Interface | float | 0 | W |  |  | T | Time For Write ChannelsInterface | IO.State.Perf | ms
;
;Timeslice timing monitoring
S_TimeForTimesliceOne | Monitor | Time For TimesliceOne | float | 0 | W |  |  | T | Time For Timeslice One | IO.State.Perf | ms
S_TimeForTracing | Monitor | Time For Tracing | float | 0 | W |  |  | T | Time For Tracing | IO.State.Perf | ms
S_TimeForCalibrateInputs | Monitor | Time For CalibrateInputs | float | 0 | W |  |  | T | Time For Calibrate Inputs | IO.State.Perf | ms
S_TimeForUpdateDerivedChannels | Monitor | Time For UpdateDerivedChannels | float | 0 | W |  |  | T | Time For Update Derived Channels | IO.State.Perf | ms
S_TimeForCalibrateOutputs | Monitor | Time For CalibrateOutputs | float | 0 | W |  |  | T | Time For CalibrateOutputs | IO.State.Perf | ms
S_TimeForUpdateStateMachines | Monitor | Time For UpdateStateMachines | float | 0 | W |  |  | T | Time For Update StateMachines | IO.State.Perf | ms
S_TimeForUpdateVspr | Monitor | Time For UpdateVspr | float | 0 | W |  |  | T | Time For Update VSPR | IO.State.Perf | ms
S_TimeForUpdateAlarms | Monitor | Time For UpdateAlarms | float | 0 | W |  |  | T | Time For UpdateAlarms | IO.State.Perf | ms
;
;Time
S_UtcTimeMilliSeconds | Vspr | Universal coordinated time in miliseconds. Milliseconds since 1st January 1970 | double | 0 | W |  |  | T
S_UtcTimeSeconds | Vspr | Universal coordinated time in seconds. Seconds since 1st January 1970 | uint | 0 | W |  |  | T
;
;Controller Supervisory Logic
S_VsprEnabled | Vspr | Control algorithm enabled | bool | false | W |  | true |  | VsprEnabled | IO.Algorithm.Control
S_ActiveMinimumPitchRate | Vspr | Pitch control algorithm control value - minimum pitch rate | float | 0 | W |  |  | A/T | ActiveMinimumPitchRate | IO.Algorithm.Control | deg/s
S_ActiveMinimumPitchAngle | Vspr | Pitch control algorithm control value - minimum pitch angle | float | 0 | W |  | true | A | ActiveMinimumPitchAngle | IO.Algorithm.Control | deg/s
S_ShutdownFlag | Vspr | Shutdown flag | bool | false | W |  |  |  | ShutdownFlag | IO.Algorithm.Control
S_ShutdownMaxTorque | Vspr | Maximum Torque during normal shutdowns | float | 0 | W |  |  | FL | ShutdownMaxTorque | IO.Algorithm.Control | N.m
S_StartupPowerFraction | Vspr | Fraction of rated power to apply durign startup | float | 0 | W |  | true |  | StartupPowerFraction | IO.Algorithm.Control
S_DisconnectedSpeedSetpointTarget | Vspr | Speed setpoint target if not in power production | float | 0 | W |  |  | A/T | DisconnectedSpeedSetpointTarget | IO.Algorithm.Control
S_LvrtOriginalMinPitchRate | Vspr | LVRT original minimum pitch rate | float | 0 | W |  |  | A/T | LvrtOriginalMinPitchRate | IO.Algorithm.Control | deg/s
S_LvrtTorqueLimitTarget | Vspr | Torque limit value to be used on Qdem in Lvrt | float | 0 | W |  |  | FL | LvrtTorqueLimitTarget | IO.Algorithm.Control | N.m
S_LvrtTorqueLimit | Vspr | Torque limit value to be used on Qdem in Lvrt (upward rate limited) | float | 0 | W |  |  | FL | LvrtTorqueLimit | IO.Algorithm.Control | N.m
S_InitFastShutdown | Vspr | Initiating fast shut down | bool | false | W |  |  |  | InitFastshutdown | IO.Algorithm.Control
;
;Pitch Control
S_VsprMeasuredMeanPitch | Vspr | Measured Mean Pitch | float | 0 | W |  | true | A | VsprMeasuredMeanPitch | IO.Algorithm.PitchControl
S_VsprMeasuredSpeedPitch | Vspr | Measured Speed for Pitch Loop | float | 0 | W |  | true | A/T | VsprMeasuredSpeedPitch | IO.Algorithm.PitchControl
S_VsprFilteredSpeedPitch | Vspr | Filtered Speed Pitch | float | 0 | W |  | true | A/T | VsprFilteredSpeedPitch | IO.Algorithm.PitchControl
S_VsprSpeedSetpointPitch | Vspr | Speed Setpoint Pitch | float | 0 | W | true | true | A/T | VsprSpeedSetpointPitch | IO.Algorithm.PitchControl
S_VsprFilteredSpeedErrorPitch | Vspr | Filtered Speed Error Pitch | float | 0 | W |  | true | A/T | VsprFilteredSpeedErrorPitch | IO.Algorithm.PitchControl
S_VsprPitchBias | Vspr | Speed Set Point Bias Pitch | float | 0 | W | true | true | A/T | VsprPitchBias | IO.Algorithm.PitchControl
S_VsprPitchDemand | Vspr | Pitch Demand | float | 0 | W |  | true | A | VsprPitchDemand | IO.Algorithm.PitchControl
S_VsprIncreasedPitchSpeedGains | Vspr | Increased Gain Flag due to large speed error and acceleration | bool | false | W |  | true |  | VsprIncreasedPitchSpeedGains | IO.Algorithm.PitchControl
S_VsprEEdot | Vspr | Eedot (does not include effect of PitchBias as in PID) | float | 0 | W |  | true | AA/TTT | VsprEEdot | IO.Algorithm.PitchControl
S_VsprPitchRateDemandCollective | Vspr | Collective Pitch Rate Demand | float | 0 | W |  | true | A/T | VsprPitchRateDemandCollective | IO.Algorithm.PitchControl
S_VsprMinimumPitch | Vspr | Minimum Pitch | float | 0 | W | true | true | A | VsprMinimumPitch | IO.Algorithm.PitchControl
S_VsprMinimumPitchRate | Vspr | Minimum Pitch Rate | float | 0 | W |  | true | A/T | VsprMinimumPitchRate | IO.Algorithm.PitchControl
S_VsprMaximumPitchRate | Vspr | Maximum Pitch Rate | float | 0 | W |  | true | A/T | VsprMaximumPitchRate | IO.Algorithm.PitchControl
S_VsprGainSchedule | Vspr | Gain Schedule | float | 0 | W |  | true |  | VsprGainSchedule | IO.Algorithm.PitchControl
S_VsprDyExtra | Vspr | DyExtra | float | 0 | W |  | true | A | VsprDyExtra | IO.Algorithm.PitchControl
S_VsprDyRateExtra | Vspr | DyRateExtra | float | 0 | W |  | true | A/T | VsprDyRateExtra | IO.Algorithm.PitchControl
S_VsprPidKp | Vspr | Pid.Kp | float | 0 | W |  | true |  | VsprPidKp | IO.Algorithm.PitchControl
S_VsprPidKi | Vspr | Pid Ki | float | 0 | W |  | true | 1/T | VsprPidKi | IO.Algorithm.PitchControl
S_VsprPidKp2 | Vspr | Pid.Kp2 | float | 0 | W |  | true |  | VsprPidKp2 | IO.Algorithm.PitchControl
S_VsprPidKi2 | Vspr | Pid Ki2 | float | 0 | W |  | true | 1/T | VsprPidKi2 | IO.Algorithm.PitchControl
S_VsprPidKpFast | Vspr | Pid.KpFast | float | 0 | W |  | true |  | VsprPidKpFast | IO.Algorithm.PitchControl
S_VsprPidKiFast | Vspr | Pid KiFast | float | 0 | W |  |  | 1/T | VsprPidKiFast | IO.Algorithm.PitchControl
S_VsprPidKd | Vspr | Pid Kd | float | 0 | W |  |  | T | VsprPidKd | IO.Algorithm.PitchControl
S_VsprPidNum0 | Vspr | Pid Num 0 | float | 0 | W |  |  | T | VsprPidNum0 | IO.Algorithm.PitchControl
S_VsprPidNum1 | Vspr | Pid Num 1 | float | 0 | W |  |  | T | VsprPidNum1 | IO.Algorithm.PitchControl
S_VsprPidNum2 | Vspr | Pid Num 2 | float | 0 | W |  |  | T | VsprPidNum2 | IO.Algorithm.PitchControl
S_VsprErrSchedX | Vspr | Error Schedule Input (XXDot) | float | 0 | W |  |  | AA/TTT | VsprErrSchedX | IO.Algorithm.PitchControl
S_VsprErrSchedNonlinearGainFactor | Vspr | Error Schedule Nonlinear gain factor | float | 0 | W |  |  |  | VsprErrSchedNonlinearGainFactor | IO.Algorithm.PitchControl
S_rPower | Vspr | S_rPower | float | 0 | W |  | true | p | rPower
S_VsprFinePitchPower | Vspr | Fine pitch from power | float | 0 | W |  | true | A | VsprFinePitchPower | IO.Algorithm.PitchControl
S_VsprFinePitchYaw | Vspr | Fine pitch from yaw error | float | 0 | W |  | true | A | VsprFinePitchYaw | IO.Algorithm.PitchControl
S_VsprFinePitchDynamic | Vspr | Dynamic Fine Pitch | float | 0 | W |  | true | A | VsprFinePitchDynamic | IO.Algorithm.PitchControl
S_ExpectedPitchAngle1 | Pitch | Expected Pitch Position Blade 1 | float | 0 | W | true |  | A | ExpectedPitchAngle1 | IO.Algorithm.PitchControl
S_ExpectedPitchAngle2 | Pitch | Expected Pitch Position Blade 2 | float | 0 | W | true |  | A | ExpectedPitchAngle2 | IO.Algorithm.PitchControl
S_ExpectedPitchAngle3 | Pitch | Expected Pitch Position Blade 3 | float | 0 | W | true |  | A | ExpectedPitchAngle3 | IO.Algorithm.PitchControl
S_VsprIndivCorrBlade1 | Vspr | Indiv Corr Blade 1 | float | 0 | W |  |  | A/T | VsprIndivCorrBlade1 | IO.Algorithm.PitchControl
S_VsprIndivCorrBlade2 | Vspr | Indiv Corr Blade 2 | float | 0 | W |  |  | A/T | VsprIndivCorrBlade2 | IO.Algorithm.PitchControl
S_VsprIndivCorrBlade3 | Vspr | Indiv Corr Blade 3 | float | 0 | W |  |  | A/T | VsprIndivCorrBlade3 | IO.Algorithm.PitchControl
S_VsprPidPdy | Vspr | PidDy | float | 0 | W |  | true | A | VsprPidPdy | IO.Algorithm.PitchControl
S_VsprPidPdy1 | Vspr | PidPdy1 | float | 0 | W |  | true | A | VsprPidPdy1 | IO.Algorithm.PitchControl
S_VsprPidPdy2 | Vspr | PidPdy2 | float | 0 | W |  | true | A | VsprPidPdy2 | IO.Algorithm.PitchControl
S_VsprPidPdy3 | Vspr | PidPdy3 | float | 0 | W |  | true | A | VsprPidPdy3 | IO.Algorithm.PitchControl
S_VsprPid2Num0 | Vspr | Pid2 Num 0 | float | 0 | W |  | true | T | VsprPid2Num0 | IO.Algorithm.PitchControl
S_VsprPid2Num1 | Vspr | Pid2 Num 1 | float | 0 | W |  | true | T | VsprPid2Num1 | IO.Algorithm.PitchControl
S_VsprPid2Num2 | Vspr | Pid2 Num 2 | float | 0 | W |  | true | T | VsprPid2Num2 | IO.Algorithm.PitchControl
S_StartPitchRate | Vspr | Start pitch rate | float | 0 | W |  | true | T | StartPitchRate | IO.Algorithm.PitchControl | deg/s
;
;Torque Control
S_VsprMeasuredSpeedTorque | Vspr | Measured Speed for Torque Loop | float | 0 | W |  | true | A/T | VsprMeasuredSpeedTorque | IO.Algorithm.TorqueControl | rpm
S_VsprFilteredSpeedTorque | Vspr | Filtered Speed Torque | float | 0 | W |  | true | A/T | VsprFilteredSpeedTorque | IO.Algorithm.TorqueControl | rpm
S_VsprSpeedSetpointTorque | Vspr | Speed Setpoint Torque | float | 0 | W | true | true | A/T | VsprSpeedSetpointTorque | IO.Algorithm.TorqueControl | rpm
S_VsprFilteredSpeedErrorTorque | Vspr | Filtered Speed Error Torque | float | 0 | W |  | true | A/T | VsprFilteredSpeedErrorTorque | IO.Algorithm.TorqueControl | rpm
S_VsprTorqueBias | Vspr | Torque Bias | float | 0 | W | true | true | A/T | VsprTorqueBias | IO.Algorithm.TorqueControl
S_VsprWMin | Vspr | WMin | float | 0 | W |  | true | A/T | VsprWMin | IO.Algorithm.TorqueControl
S_VsprWMax | Vspr | WMax | float | 0 | W |  | true | A/T | VsprWMax | IO.Algorithm.TorqueControl
S_VsprPowDem0 | Vspr | Pow Dem 0 | float | 0 | W |  | true | P | VsprPowDem0 | IO.Algorithm.TorqueControl | kW
S_VsprPowerReference | Vspr | Power Reference | float | 0 | W |  | true | P | VsprPowerReference | IO.Algorithm.TorqueControl | kW
S_VsprQxP | Vspr | Qx P | float | 0 | W |  | true | FL | VsprQxP | IO.Algorithm.TorqueControl
S_VsprQminP | Vspr | Qmin P | float | 0 | W |  | true | FL | VsprQminP | IO.Algorithm.TorqueControl
S_VsprWmaxP | Vspr | Wmax P | float | 0 | W |  | true | A/T | VsprWmaxP | IO.Algorithm.TorqueControl
S_VsprWoptP | Vspr | Wopt P | float | 0 | W |  | true | A/T | VsprWoptP | IO.Algorithm.TorqueControl
S_VsprQtopP | Vspr | Qtop P | float | 0 | W |  | true | FL | VsprQtopP | IO.Algorithm.TorqueControl | N.m
S_VsprQdem0P | Vspr | Qdem 0P | float | 0 | W |  | true | FL | VsprQdem0P | IO.Algorithm.TorqueControl | N.m
S_VsprBandPassP | Vspr | Band Pass P | float | 0 | W |  | true | FL | VsprBandPassP | IO.Algorithm.TorqueControl | N.m
S_VsprQxFL | Vspr | Qx FL | float | 0 | W |  | true | FL | VsprQxFL | IO.Algorithm.TorqueControl | N.m
S_VsprQminFL | Vspr | Qmin FL | float | 0 | W |  | true | FL | VsprQminFL | IO.Algorithm.TorqueControl | N.m
S_VsprQmaxFL | Vspr | Qmax FL | float | 0 | W |  | true | FL | VsprQmaxFL | IO.Algorithm.TorqueControl | N.m
S_VsprQoptFL | Vspr | Qopt FL | float | 0 | W |  | true | FL | VsprQoptFL | IO.Algorithm.TorqueControl | N.m
S_VsprQtopFL | Vspr | Qtop FL | float | 0 | W |  | true | FL | VsprQtopFL | IO.Algorithm.TorqueControl | N.m
S_VsprQdem | Vspr | Qdem | float | 0 | W |  | true | FL | VsprQdem | IO.Algorithm.TorqueControl | N.m
S_VsprDampingTorque | Vspr | Damping Torque | float | 0 | W | true | true | FL | VsprDampingTorque | IO.Algorithm.TorqueControl | N.m
S_VsprTorqueDemand | Vspr | Torque Demand | float | 0 | W |  | true | FL | VsprTorqueDemand | IO.Algorithm.TorqueControl | N.m
S_VsprTorqueLimitState | Vspr | Torque Limit State | float | 0 | W | true | true |  | VsprTorqueLimitState | IO.Algorithm.TorqueControl
S_VsprAboveRatedFlag | Vspr | Above rated flag | float | 0 | W | true | true |  | VsprAboveRatedFlag | IO.Algorithm.TorqueControl
S_VsprMeasuredPower | Vspr | Measured Power | float | 0 | W |  | true | P | VsprMeasuredPower | IO.Algorithm.TorqueControl | kW
S_VsprDesiredPower | Vspr | Desired Power | float | 0 | W |  | true | P | VsprDesiredPower | IO.Algorithm.TorqueControl | kW
S_VsprTorqueCorrectError | Vspr | Torque Correct Error | float | 0 | W |  | true | P | VsprTorqueCorrectError | IO.Algorithm.TorqueControl | kW
S_VsprTorqueCorrectionFactor | Vspr | Torque Correction Factor | float | 0 | W |  | true |  | VsprTorqueCorrectionFactor | IO.Algorithm.TorqueControl
;
;Nacelle Acceleration Feedback
S_VsprMeasuredNacAccFA | Vspr | Acceleration FA Input | float | 0 | W |  |  | L/TT | VsprMeasuredNacAccFA | IO.Algorithm.NAF | m/s/s
S_VsprAccFAPitchRate | Vspr | Acceleration FA Pitch Rate | float | 0 | W | true |  | A/T | VsprAccFAPitchRate | IO.Algorithm.NAF | deg/s
S_VsprTowerAccelerationSchedule | Vspr | Tower Acceleration Schedule | float | 0 | W |  |  |  | VsprTowerAccelerationSchedule | IO.Algorithm.NAF
S_VsprAccelerationFeedbackPitch | Vspr | Acceleration Feedback Pitch | float | 0 | W |  |  | A | VsprAccelerationFeedbackPitch | IO.Algorithm.NAF
;
;Non Linear stuff | [8 empty] | on Linear stuff
S_VsprNonLinearCycleTime | Vspr |  | float | 0 | W |  | false | T | CycleTime | IO.Algorithm.NAF | s
S_VsprNonLinearAcrDyElapsedTime | Vspr |  | float | 0 | W |  | true | T | NonLinearAcrDyElapsedTime | IO.Algorithm.NAF | s
S_VsprNonLinearActionAllowed | Vspr |  | bool | true | W |  | true |  | nonLinearActionAllowed | IO.Algorithm.NAF
S_VsprNonLinearjustDidNonLinearPitchAction | Vspr |  | bool | false | W |  | true |  | justDidNonLinearPitchAction | IO.Algorithm.NAF
S_VsprNonLineardoPitchKick | Vspr |  | bool | false | W |  | true |  | doPitchKick | IO.Algorithm.NAF
S_VsprNonLinearKickDuration | Vspr |  | float | 0 | W |  | true | T | KickDuration | IO.Algorithm.NAF | s
S_VsprNonLinearKickDuration2 | Vspr |  | float | 0 | W |  | false | T | KickDuration2 | IO.Algorithm.NAF | s
S_VsprNonLinearextraPitchRate | Vspr |  | float | 0 | W |  | true | A/T | extraPitchRate | IO.Algorithm.NAF | rad/s
S_VsprNonLinearextraPitchRateEEdot | Vspr |  | float | 0 | W |  | true | A/T | extraPitchRateEEdot | IO.Algorithm.NAF | rad/s
S_VsprNonLinearextraPitchRateNL | Vspr |  | float | 0 | W |  | false | A/T | extraPitchRateNL | IO.Algorithm.NAF | rad/s
S_VsprextraPitchRateGenAccPA | Vspr |  | float | 0 | W |  | false | A/T | extraPitchRateGenaccPA | IO.Algorithm.NAF | rad/s
S_VsprNonLinearExtraPitchRateGenAcc | Vspr |  | float | 0 | W |  | false | A/T | extraPitchRateGenAcc | IO.Algorithm.NAF | rad/s
S_VsprNonLinearEEdotSchedulingVariable | Vspr |  | float | 0 | W |  | true |  | EEdotSchedulingVar | IO.Algorithm.NAF | rad^2/s^3
S_VsprNonLinearEEdotThreshold | Vspr |  | float | 0 | W |  | true |  | EEdotThreshold | IO.Algorithm.NAF | rad^2/s^3
S_VsprNonLinearEEdotThresholdAsymMovAv | Vspr |  | float | 0 | W |  | true |  | EEdotThresholdAsymMovAv | IO.Algorithm.NAF | rad^2/s^3
S_VsprNonLinearisEEdotAboveThreshold | Vspr |  | bool | false | W |  | true |  | isEEdotAboveThreshold | IO.Algorithm.NAF
S_VsprNonLinearisYawPitchKickAllowed | Vspr |  | bool | false | W |  | false |  | isYawPitchKickThreshold | IO.Algorithm.NAF
S_VsprNonLinearMeasuredPowerAcceleration | Vspr |  | float | 0 | W |  | false | P | MeasuredPowerAcceleration | IO.Algorithm.NAF | W/s
S_VsprNonLinearPitchdemand | Vspr |  | float | 0 | W |  | false | A/T | *PitchRateDemand | IO.Algorithm.NAF | rad/s
S_VsprNonLinearMinGenSpeedErrorLimit | Vspr |  | float | 0 | W |  | false | A/T | MinGenSpeedErrorLimit | IO.Algorithm.NAF | rad/s
S_VsprNonLinearSpeedVariable | Vspr |  | float | 0 | W |  | false | A/T | NonLinearSpeedVariable | IO.Algorithm.NAF | rad/s
S_VsprNonLinearrAccFilteredNL | Vspr |  | float | 0 | W |  | false | L/TT | rAccFilteredNL | IO.Algorithm.NAF | m/s^2
S_VsprNonLinearAccThreshold | Vspr |  | float | 0 | W |  | false |  | NonLinearThreshold | IO.Algorithm.NAF | -
S_VsprNonLinearAccVariable | Vspr |  | float | 0 | W |  | false |  | nonLinearAcrDy_SchedulingVariable | IO.Algorithm.NAF | -
S_VsprNonLinearisNLaxAboveThreshold | Vspr |  | bool | false | W |  | false |  | isNLaxAboveThreshold | IO.Algorithm.NAF
S_VsprNonLinearNL2Threshold | Vspr |  | float | 0 | W |  | false |  | NonLinearNL2Threshold | IO.Algorithm.NAF | -
S_VsprNonLinearQdemFilt | Vspr |  | float | 0 | W |  | false | FL | QdemFilt | IO.Algorithm.NAF | Nm
S_VsprNonLinearGeneratorFilteredAcc | Vspr |  | float | 0 | W |  | false | A/TT | GeneratorFilteredAcceleration | IO.Algorithm.NAF | rad/s^2
S_VsprNonLinearGenAccPitchAngleThreshold | Vspr |  | float | 0 | W |  | false | A/TT | GenAccPitchAngleThreshold | IO.Algorithm.NAF | rad/s^2
S_VsprNonLinearisGenAccPitchAngleThreshold | Vspr |  | bool | false | W |  | false |  | isGenAccPitchAngleThreshold | IO.Algorithm.NAF
S_VsprNonLinearGenAccThreshold | Vspr |  | float | 0 | W |  | false | A/TT | GeneratorAccThresholdAfterDelay | IO.Algorithm.NAF | rad/s^2
S_VsprNonLinearcrossedThreshold | Vspr |  | bool | false | W |  | false |  | crossedThreshold | IO.Algorithm.NAF
S_VsprNonLinearincrementTimer | Vspr |  | bool | false | W |  | false |  | incrementTimer | IO.Algorithm.NAF
S_VsprNonLineartimeSinceCrossing | Vspr |  | float | 0 | W |  | false | T | timeSinceCrossing | IO.Algorithm.NAF | s
S_VsprNonLinearcrossedGenAccThreshold | Vspr |  | bool | false | W |  | false |  | crossedGenAccThreshold | IO.Algorithm.NAF
;
;IPC
S_IpcMaxDiff | Vspr | 2P IPC Maximum Diff Pitch | float | 0 | W |  | false | A | IpcMaxDiff | IO.Algorithm.IPC | deg
S_IpcCalculateThreshold | Vspr | IPC Calculate Threshold | float | 0 | W |  | true | FL | IpcCalculateThreshold | IO.Algorithm.IPC | N.m
S_IpcDAxisMy | Vspr | IPC D Axis My | float | 0 | W |  | false | FL | IpcDAxisMy | IO.Algorithm.IPC | N.m
S_IpcQAxisMy | Vspr | IPC Q Axis My | float | 0 | W |  | false | FL | IpcQAxisMy | IO.Algorithm.IPC | N.m
S_IpcFilteredDAxisMy | Vspr | IPC Filtered D Axis My | float | 0 | W |  | false | FL | IpcFilteredDAxisMy | IO.Algorithm.IPC | N.m
S_IpcFilteredQAxisMy | Vspr | IPC Filtered Q Axis My | float | 0 | W |  | false | FL | IpcFilteredQAxisMy | IO.Algorithm.IPC | N.m
S_IpcDAxisPitchDemand | Vspr | IPC D Axis Pitch Angle Demand | float | 0 | W |  | false | A | IpcDAxisPitchDemand | IO.Algorithm.IPC | deg
S_IpcQAxisPitchDemand | Vspr | IPC Q Axis Pitch Angle Demand | float | 0 | W |  | false | A | IpcQAxisPitchDemand | IO.Algorithm.IPC | deg
S_IpcDAxisPitchDemTimeShifted | Vspr | IPC D Axis Pitch Angle Demand Time Shifted | float | 0 | W |  | false | A | IpcDAxisPitchDemTimeShifted | IO.Algorithm.IPC | deg
S_IpcQAxisPitchDemTimeShifted | Vspr | IPC Q Axis Pitch Angle Demand Time Shifted | float | 0 | W |  | false | A | IpcQAxisPitchDemTimeShifted | IO.Algorithm.IPC | deg
S_IpcDAxisMeasuredPitch | Vspr | IPC D Axis Measured Pitch Angle | float | 0 | W |  | false | A | IpcDAxisMeasuredPitch | IO.Algorithm.IPC | deg
S_IpcQAxisMeasuredPitch | Vspr | IPC Q Axis Measured Pitch Angle | float | 0 | W |  | false | A | IpcQAxisMeasuredPitch | IO.Algorithm.IPC | deg
S_IpcMeasuredMy1 | Vspr | IPC Measured My Blade 1 | float | 0 | W |  | false | FL | IpcMeasuredMy1 | IO.Algorithm.IPC | N.m
S_IpcMeasuredMy2 | Vspr | IPC Measured My Blade 2 | float | 0 | W |  | false | FL | IpcMeasuredMy2 | IO.Algorithm.IPC | N.m
S_IpcMeasuredMy3 | Vspr | IPC Measured My Blade 3 | float | 0 | W |  | false | FL | IpcMeasuredMy3 | IO.Algorithm.IPC | N.m
S_IpcFilteredMy1 | Vspr | IPC Filtered My Blade 1 | float | 0 | W |  | false | FL | IpcFilteredMy1 | IO.Algorithm.IPC | N.m
S_IpcFilteredMy2 | Vspr | IPC Filtered My Blade 2 | float | 0 | W |  | false | FL | IpcFilteredMy2 | IO.Algorithm.IPC | N.m
S_IpcFilteredMy3 | Vspr | IPC Filtered My Blade 3 | float | 0 | W |  | false | FL | IpcFilteredMy3 | IO.Algorithm.IPC | N.m
S_IpcPitchDemand1 | Vspr | IPC pitch demand 1 | float | 0 | W |  | false | A | IpcPitchDemand1 | IO.Algorithm.IPC | deg
S_IpcPitchDemand2 | Vspr | IPC pitch demand 2 | float | 0 | W |  | false | A | IpcPitchDemand2 | IO.Algorithm.IPC | deg
S_IpcPitchDemand3 | Vspr | IPC pitch demand 3 | float | 0 | W |  | false | A | IpcPitchDemand3 | IO.Algorithm.IPC | deg
S_IpcPitchRateDemand1 | Vspr | IPC pitch rate demand 1 | float | 0 | W |  | false | A/T | IpcPitchRateDemand1 | IO.Algorithm.IPC | deg/s
S_IpcPitchRateDemand2 | Vspr | IPC pitch rate demand 2 | float | 0 | W |  | false | A/T | IpcPitchRateDemand2 | IO.Algorithm.IPC | deg/s
S_IpcPitchRateDemand3 | Vspr | IPC pitch rate demand 3 | float | 0 | W |  | false | A/T | IpcPitchRateDemand3 | IO.Algorithm.IPC | deg/s
S_IpcDAxisPitchRateDemand | Vspr | D-axis pitch rate demand | float | 0 | W |  | false | A/T | IpcDAxisPitchRateDemand | IO.Algorithm.IPC | deg/s
S_IpcQAxisPitchRateDemand | Vspr | Q-axis pitch rate demand | float | 0 | W |  | false | A/T | IpcQAxisPitchRateDemand | IO.Algorithm.IPC | deg/s
S_PitLimDiff | Vspr | S_PitLimDiff | float | 0 | W |  | false | A | PitLimDiff
;
;2P IPC
S_2PIpcMaxDiff | Vspr | 2P IPC Maximum Diff Pitch | float | 0 | W |  | false | A | 2PIpcMaxDiff | IO.Algorithm.2PIPC | deg
S_2PIpcDAxisMaxDiff | Vspr | 2P IPC Maximum Diff Pitch | float | 0 | W |  | false | A | 2PIpcDAxisMaxDiff | IO.Algorithm.2PIPC | deg
S_2PIpcQAxisMaxDiff | Vspr | 2P IPC Maximum Diff Pitch | float | 0 | W |  | false | A | 2PIpcQAxisMaxDiff | IO.Algorithm.2PIPC | deg
S_2PIpcMaxAbsPitchRateDemand | Vspr | 2P IPC Maximum absolute Pitch rate demand across all blades | float | 0 | W |  | false | A/T | 2PIpcMaxAbsPitchRateDemand | IO.Algorithm.2PIPC | deg/s
S_2PIpcMaxAbsPitchRateDemandFilt | Vspr | 2P IPC Maximum absolute Pitch rate demand across all blades filtered | float | 0 | W |  | false | A/T | 2PIpcMaxAbsPitchRateDemandFilt | IO.Algorithm.2PIPC | deg/s
S_2PIpcGs | Vspr | 2P IPC GS gain for PIDs | float | 0 | W |  | false |  | 2PIpcGs | IO.Algorithm.2PIPC
S_2PIpcDAxisMy | Vspr | 2P IPC D Axis My | float | 0 | W |  | false | FL | 2PIpcDAxisMy | IO.Algorithm.2PIPC | N.m
S_2PIpcQAxisMy | Vspr | 2P IPC Q Axis My | float | 0 | W |  | false | FL | 2PIpcQAxisMy | IO.Algorithm.2PIPC | N.m
S_2PIpcFilteredDAxisMy | Vspr | 2P IPC Filtered D Axis My | float | 0 | W |  | false | FL | 2PIpcFilteredDAxisMy | IO.Algorithm.2PIPC | N.m
S_2PIpcFilteredQAxisMy | Vspr | 2P IPC Filtered Q Axis My | float | 0 | W |  | false | FL | 2PIpcFilteredQAxisMy | IO.Algorithm.2PIPC | N.m
S_2PIpcDAxisPitchDemand | Vspr | 2P IPC D Axis Pitch Angle Demand | float | 0 | W |  | false | A | 2PIpcDAxisPitchDemand | IO.Algorithm.2PIPC | deg
S_2PIpcQAxisPitchDemand | Vspr | 2P IPC Q Axis Pitch Angle Demand | float | 0 | W |  | false | A | 2PIpcQAxisPitchDemand | IO.Algorithm.2PIPC | deg
S_2PIpcDAxisPitchDemTimeShifted | Vspr | 2P IPC D Axis Pitch Angle Demand Time Shifted | float | 0 | W |  | false | A | 2PIpcDAxisPitchDemTimeShifted | IO.Algorithm.2PIPC | deg
S_2PIpcQAxisPitchDemTimeShifted | Vspr | 2P IPC Q Axis Pitch Angle Demand Time Shifted | float | 0 | W |  | false | A | 2PIpcQAxisPitchDemTimeShifted | IO.Algorithm.2PIPC | deg
S_2PIpcDAxisMeasuredPitch | Vspr | 2P IPC D Axis Measured Pitch Angle | float | 0 | W |  | false | A | 2PIpcDAxisMeasuredPitch | IO.Algorithm.2PIPC | deg
S_2PIpcQAxisMeasuredPitch | Vspr | 2P IPC Q Axis Measured Pitch Angle | float | 0 | W |  | false | A | 2PIpcQAxisMeasuredPitch | IO.Algorithm.2PIPC | deg
S_2PIpcMeasuredMy1 | Vspr | 2P IPC Measured My Blade 1 | float | 0 | W |  | false | FL | 2PIpcMeasuredMy1 | IO.Algorithm.2PIPC | N.m
S_2PIpcMeasuredMy2 | Vspr | 2P IPC Measured My Blade 2 | float | 0 | W |  | false | FL | 2PIpcMeasuredMy2 | IO.Algorithm.2PIPC | N.m
S_2PIpcMeasuredMy3 | Vspr | 2P IPC Measured My Blade 3 | float | 0 | W |  | false | FL | 2PIpcMeasuredMy3 | IO.Algorithm.2PIPC | N.m
S_2PIpcFilteredMy1 | Vspr | 2P IPC Filtered My Blade 1 | float | 0 | W |  | false | FL | 2PIpcFilteredMy1 | IO.Algorithm.2PIPC | N.m
S_2PIpcFilteredMy2 | Vspr | 2P IPC Filtered My Blade 2 | float | 0 | W |  | false | FL | 2PIpcFilteredMy2 | IO.Algorithm.2PIPC | N.m
S_2PIpcFilteredMy3 | Vspr | 2P IPC Filtered My Blade 3 | float | 0 | W |  | false | FL | 2PIpcFilteredMy3 | IO.Algorithm.2PIPC | N.m
S_2PIpcPitchDemand1 | Vspr | 2P IPC pitch demand 1 | float | 0 | W |  | false | A | 2PIpcPitchDemand1 | IO.Algorithm.IPC | N.m
S_2PIpcPitchDemand2 | Vspr | 2P IPC pitch demand 2 | float | 0 | W |  | false | A | 2PIpcPitchDemand2 | IO.Algorithm.IPC | N.m
S_2PIpcPitchDemand3 | Vspr | 2P IPC pitch demand 3 | float | 0 | W |  | false | A | 2PIpcPitchDemand3 | IO.Algorithm.IPC | N.m
S_2PIpcPitchRateDemand1 | Vspr | 2P IPC pitch rate demand 1 | float | 0 | W |  | false | A/T | 2PIpcPitchRateDemand1 | IO.Algorithm.IPC | N.m
S_2PIpcPitchRateDemand2 | Vspr | 2P IPC pitch rate demand 2 | float | 0 | W |  | false | A/T | 2PIpcPitchRateDemand2 | IO.Algorithm.IPC | N.m
S_2PIpcPitchRateDemand3 | Vspr | 2P IPC pitch rate demand 3 | float | 0 | W |  | false | A/T | 2PIpcPitchRateDemand3 | IO.Algorithm.IPC | N.m
S_2PIpcDAxisPitchRateDemand | Vspr | 2P D-axis pitch rate demand | float | 0 | W |  | false | A/T | 2PIpcDAxisPitchRateDemand | IO.Algorithm.IPC | deg/s
S_2PIpcQAxisPitchRateDemand | Vspr | 2P Q-axis pitch rate demand | float | 0 | W |  | false | A/T | 2PIpcQAxisPitchRateDemand | IO.Algorithm.IPC | deg/s
;
;IPC Limits
S_IpcDiffPitchFactorTorque | Vspr | IPC Diff Pitch Factor From Torque | float | 0 | W |  |  |  | IpcDiffPitchFactorTorque | IO.Algorithm.IPCLimits
S_IpcDiffPitchFactorMaximumPitch | Vspr | IPC Diff Pitch Factor from Maximum Pitch Angle | float | 0 | W |  |  |  | IpcDiffPitchFactorMaximumPitch | IO.Algorithm.IPCLimits
S_IpcDiffPitchFactorMinimumPitch | Vspr | IPC Diff Pitch Factor from Minimum Pitch Angle | float | 0 | W |  |  |  | IpcDiffPitchFactorMinimumPitch | IO.Algorithm.IPCLimits
S_IpcFilteredGenAcc | Vspr | IPC Filtered Generator Acceleration for schedule | float | 0 | W |  |  | A/TT | IpcFilteredGenAcc | IO.Algorithm.IPCLimits | rpm
S_IpcDiffPitchFactorGenAcc | Vspr | IPC Diff Pitch Factor From Generator Acceleration | float | 0 | W |  |  |  | IpcDiffPitchFactorGenAcc | IO.Algorithm.IPCLimits
S_IpcDiffPitchFactorPitchRate | Vspr | IPC Diff Pitch Factor from Pitch Rate | float | 0 | W |  |  |  | IpcDiffPitchFactorPitchRate | IO.Algorithm.IPCLimits
S_IpcMinDiffPitchFactorYawErr | Vspr | IPC Min Diff Pitch Factor From Yaw Error | float | 0 | W |  |  |  | IpcMinDiffPitchFactorYawErr | IO.Algorithm.IPCLimits
S_IpcMaxDiffFactor | Vspr | IPC Maximum Diff Pitch | float | 0 | W |  |  |  | IpcMaxDiffFactor | IO.Algorithm.IPCLimits
;IPC Limits with blade bending moment | [8 empty] | PC Limits with blade bending moment
S_MaximumBladeBendingMoment | Vspr |  | float | 0 |  |  |  | FL | MaximumBladeBendingMoment | IO.Algorithm.IPCLimits | N.m
S_TimeQAxisMyUpDuration | Vspr |  | float | 0 |  |  | false |  | TimeQAxisMyUpDuration | IO.Algorithm.IPCLimits
S_QAxisMyMorethanThreshold | Vspr |  | bool | false |  |  | false |  | QAxisMyMorethanThreshold | IO.Algorithm.IPCLimits
S_TimeSinceIPC | Vspr |  | float | 0 |  |  |  |  | TimeSinceIPC | IO.Algorithm.IPCLimits | s
S_IPCSustainedTimer | Vspr |  | float | true |  |  |  |  | IPCSustainedTimer | IO.Algorithm.IPCLimits
S_IPCEnabledFlag | Vspr |  | float | false |  |  |  |  | IPCEnabledFlag | IO.Algorithm.IPCLimits
;
;Derating
S_TimeSinceYawDerating | Vspr |  | float | 0 | W |  | true |  | TimeSinceYawDerating | IO.Algorithm.IPCLimits | s
S_YawDeratingTimer | Vspr |  | bool | false | W |  | true |  | YawDeratingTimer | IO.Algorithm.IPCLimits
S_YawDeratingFlag | Vspr |  | bool | false | W |  | true |  | YawDeratingFlag | IO.Algorithm.IPCLimits
S_YawDeratingStopMode | Vspr |  | bool | false | W |  | true |  | YawDeratingStopMode | IO.Algorithm.IPCLimits
S_bNacAccXAlarmValue | Vspr |  | bool | false | W |  | true |  | Nacelle Acceleration Fore-aft Derating flag | IO.Algorithm.IPCLimits
S_TimeSinceNacAccXDerating | Vspr |  | float | 0 | W |  | true | T | Nacelle Acceleration Fore-aft Derating Time | IO.Algorithm.IPCLimits | s
S_NacAccXDeratingFlag | Vspr |  | bool | false | W |  | true |  | Nacelle Acceleration Fore-aft Derating flag | IO.Algorithm.IPCLimits
S_TimeSinceTurDerating | Vspr |  | float | 0 | W |  | true |  | TimeSinceTurDerating | IO.Algorithm.Control | s
S_TurDeratingCounter | Vspr |  | int | 0 | W |  | true |  | TurDeratingCounter | IO.Algorithm.Control
S_TurDeratingTimer | Vspr |  | bool | false | W |  | true |  | TurDeratingTimer | IO.Algorithm.Control
S_TurDeratingFlag | Vspr |  | bool | false | W |  | true |  | TurDeratingFlag | IO.Algorithm.Control
S_HighWindDeratingFlag | Vspr |  | bool | false | W |  | true |  | S_HighWindDeratingFlag | IO.Algorithm.Control
S_DeratingPowerTarget | Vspr |  | float | 0 | W |  | true | P | DeratingPowerTarget | IO.Algorithm.IPCLimits | kW
S_TargetSpeedFactor | Vspr |  | float | 0 | W |  |  |  | DeratingSpeedTargetFactor | IO.Algorithm.IPCLimits
S_YawErrorPowerTarget | Vspr |  | float | 0 | W |  | true | P | YawErrorPowerTarget | IO.Algorithm.IPCLimits | kW
S_NacAccXPowerTarget | Vspr |  | float | 0 | W |  | true | P | NacAccXPowerTarget | IO.Algorithm.IPCLimits | kW
S_TurPowerTarget | Vspr |  | float | 0 | W |  | true | P | TurPowerTarget | IO.Algorithm.IPCLimits | kW
S_HighWindPowerTarget | Vspr |  | float | 0 | W |  | true | P | HighWindPowerTarget | IO.Algorithm.IPCLimits | kW
S_HighWindSpeedTarget | Vspr |  | float | 0 | W |  | true | P | HighWindSpeedTarget | IO.Algorithm.IPCLimits | kW
;
;Nacelle Acceleration X Pitch Schedule
S_NacAccXPitTarget | Vspr |  | float | 0 | W |  | false | A
S_NacAccXPitTargetRateLimited | Vspr |  | float | 0 | W |  | false | A
;
;Lidar info
S_LidarMeasuredSpeed10 | Vspr | LidarMeasuredSpeed10 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed10 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed11 | Vspr | LidarMeasuredSpeed11 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed11 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed12 | Vspr | LidarMeasuredSpeed12 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed12 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed13 | Vspr | LidarMeasuredSpeed13 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed13 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed14 | Vspr | LidarMeasuredSpeed14 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed14 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed20 | Vspr | LidarMeasuredSpeed20 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed20 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed21 | Vspr | LidarMeasuredSpeed21 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed21 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed22 | Vspr | LidarMeasuredSpeed22 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed22 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed23 | Vspr | LidarMeasuredSpeed23 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed23 | IO.Algorithm.PitchControl
S_LidarMeasuredSpeed24 | Vspr | LidarMeasuredSpeed24 | float | 0 | W |  | false | L/T | LidarMeasuredSpeed24 | IO.Algorithm.PitchControl
S_LidarRAWSPlane0 | Vspr | S_LidarRAWSPlane0 | float | 0 | W |  | false | L/T | LidarRAWSPlane0 | IO.Algorithm.PitchControl
S_LidarRAWSPlane1 | Vspr | S_LidarRAWSPlane1 | float | 0 | W |  | false | L/T | LidarRAWSPlane1 | IO.Algorithm.PitchControl
S_LidarRAWSPlane2 | Vspr | S_LidarRAWSPlane2 | float | 0 | W |  | false | L/T | LidarRAWSPlane2 | IO.Algorithm.PitchControl
S_LidarRAWSPlane3 | Vspr | S_LidarRAWSPlane3 | float | 0 | W |  | false | L/T | LidarRAWSPlane3 | IO.Algorithm.PitchControl
S_LidarRAWSPlane4 | Vspr | S_LidarRAWSPlane4 | float | 0 | W |  | false | L/T | LidarRAWSPlane4 | IO.Algorithm.PitchControl
S_LidarV0L | Vspr | S_LidarV0L | float | 0 | W |  | false | L/T | LidarV0L | IO.Algorithm.PitchControl
S_LidarV0LFiltered | Vspr | LidarV0LFiltered | float | 0 | W |  | false | L/T | LidarV0LFiltered | IO.Algorithm.PitchControl
S_LidarV0LFilteredDot | Vspr | LidarV0LFilteredDot | float | 0 | W |  | false | L/T | LidarV0LFilteredDot | IO.Algorithm.PitchControl
S_LidarV0LBuffer | Vspr | LidarV0LBuffer | float | 0 | W |  | false | L/T | LidarV0LBuffer | IO.Algorithm.PitchControl
S_LidarV0LBufferDot | Vspr | LidarV0LBufferDot | float | 0 | W |  | false | L/T
S_LidarBeamUpdate | Vspr | LidarBeamUpdate | int | 0 | W |  | false |  | LidarBeamUpdate | IO.Algorithm.PitchControl
S_LidarBeam0OccludedStatus | Vspr | LidarBeam0OccludedStatus | int | 0 | W |  | false |  | LidarBeam0OccludedStatus | IO.Algorithm.PitchControl
S_LidarBeam1OccludedStatus | Vspr | LidarBeam1OccludedStatus | int | 0 | W |  | false |  | LidarBeam1OccludedStatus | IO.Algorithm.PitchControl
S_LidarBeam2OccludedStatus | Vspr | LidarBeam2OccludedStatus | int | 0 | W |  | false |  | LidarBeam2OccludedStatus | IO.Algorithm.PitchControl
S_LidarBeam3OccludedStatus | Vspr | LidarBeam3OccludedStatus | int | 0 | W |  | false |  | LidarBeam3OccludedStatus | IO.Algorithm.PitchControl
S_LidarBeam4OccludedStatus | Vspr | LidarBeam4OccludedStatus | int | 0 | W |  | false |  | LidarBeam4OccludedStatus | IO.Algorithm.PitchControl
S_LidarLogTime | Vspr | LidarLogTime | float | 0 | W |  | false | T | LidarLogTime | IO.Algorithm.PitchControl
S_TimeTaylor | Vspr | TimeTaylor | float | 0 | W |  | false | T | TimeTaylor | IO.Algorithm.PitchControl
S_TBuffer | Vspr | Tbuffer | float | 0 | W |  | false | T | TBuffer | IO.Algorithm.PitchControl
S_LidarBeamAngleY0 | Vspr | LidarBeamAngleY0 | float | 0 | W |  | false | A | LidarBeamAngleY0 | IO.Algorithm.2PIPC | deg
S_LidarBeamAngleY1 | Vspr | LidarBeamAngleY1 | float | 0 | W |  | false | A | LidarBeamAngleY1 | IO.Algorithm.3PIPC | deg
S_LidarBeamAngleY2 | Vspr | LidarBeamAngleY2 | float | 0 | W |  | false | A | LidarBeamAngleY2 | IO.Algorithm.4PIPC | deg
S_LidarBeamAngleY3 | Vspr | LidarBeamAngleY3 | float | 0 | W |  | false | A | LidarBeamAngleY3 | IO.Algorithm.5PIPC | deg
S_LidarBeamAngleZ0 | Vspr | LidarBeamAngleZ0 | float | 0 | W |  | false | A | LidarBeamAngleZ0 | IO.Algorithm.6PIPC | deg
S_LidarBeamAngleZ1 | Vspr | LidarBeamAngleZ1 | float | 0 | W |  | false | A | LidarBeamAngleZ1 | IO.Algorithm.7PIPC | deg
S_LidarBeamAngleZ2 | Vspr | LidarBeamAngleZ2 | float | 0 | W |  | false | A | LidarBeamAngleZ2 | IO.Algorithm.8PIPC | deg
S_LidarBeamAngleZ3 | Vspr | LidarBeamAngleZ3 | float | 0 | W |  | false | A | LidarBeamAngleZ3 | IO.Algorithm.9PIPC | deg
S_LidarBeamControlCoordinateSystem | Vspr | LidarBeamAngleZ3 | int | 0 | W |  | false |  | LidarBeamControlCoordinateSystem | IO.Algorithm.PitchControl
S_LidarTransientModel | Vspr | LidarTransientModel or not | bool | false | W |  | true |  | LidarTransientModel | IO.Algorithm.PitchControl
S_LidarTransientNstep | Vspr | LidarTransientNstep | int | 0 | W |  | true |  | LidarTransientNstep | IO.Algorithm.PitchControl
S_LidarV0LMovAv | Vspr | LidarV0LMovAv | float | 0 | W |  | true | L/T | LidarV0LMovAv | IO.Algorithm.PitchControl
S_LidarV0LMovAvNstep | Vspr | LidarV0LMovAv | float | 0 | W |  | true | L/T | LidarV0LMovAvNstep | IO.Algorithm.PitchControl
S_LidarGustArea | Vspr | LidarGustArea | float | 0 | W |  | true | L | LidarGustArea | IO.Algorithm.PitchControl
S_GustState | Vspr | GustState:1.up gust; 0.no gust; -1.down gust | int | 0 | W |  | true |  | GustState | IO.Algorithm.PitchControl
S_GRTExtraPitchRate | Vspr | Gust Up ExtraPitchRate | float | 0 | W |  | true | A/T | GRTExtraPitchRate | IO.Algorithm.PitchControl
S_GRTDynFinePitchTriggered | Vspr | 1.Gust Down Dynamic fine pitch Triggered; 0.not | bool | false | W |  | true |  | GRTDynFinePitchTriggered | IO.Algorithm.PitchControl
S_GRTextraPitchRatePrevious | Vspr | Gust Up ExtraPitchRatePrevious | float | 0 | W |  | true | A/T | GRTextraPitchRatePrevious | IO.Algorithm.PitchControl
S_GRTextraPitchRatePresent | Vspr | Gust Up ExtraPitchRatePresent | float | 0 | W |  | true | A/T | GRTextraPitchRatePresent | IO.Algorithm.PitchControl
S_GRTextraPitchRateFinal | Vspr | Gust Up ExtraPitchRateFinal | float | 0 | W |  | true | A/T | GRTextraPitchRateFinal | IO.Algorithm.PitchControl
S_GRTDynamicFinePitch | Vspr | GRTDynamicFinePitch | float | 0 | W |  | true | A | GRTDynamicFinePitch | IO.Algorithm.PitchControl
S_GRTExtraTimeState | Vspr | GRTExtraTimeState | bool | false | W |  | true |  | isGustUpDetectedOff | IO.Algorithm.PitchControl
S_LidarShearV0L1 | Vspr | LidarDataProcessShearV.cpp | float | 0 | W |  | true | L/T | LidarShearV0L1 | IO.Algorithm.PitchControl
S_LidarShearV0L2 | Vspr | LidarDataProcessShearV.cpp | float | 0 | W |  | true | L/T | LidarShearV0L2 | IO.Algorithm.PitchControl
S_LidarV0LShearfliter1 | Vspr | LidarShearV.cpp LidarV0LShearfliter1 | float | 0 | W |  | true | L/T | V0L_Shear1 | IO.Algorithm.PitchControl
S_LidarV0LShearfliter2 | Vspr | LidarShearV.cpp LidarV0LShearfliter2 | float | 0 | W |  | true | L/T | V0L_Shear2 | IO.Algorithm.PitchControl
S_LidarShearArea | Vspr | LidarShearV.cpp ShearArea | float | 0 | W |  | true | L | LidarShearArea | IO.Algorithm.PitchControl
S_LidarShearAreaGust1 | Vspr | LidarShearV.cpp ShearArea | float | 0 | W |  | true | L | LidarShearAreaGust1 | IO.Algorithm.PitchControl
S_LidarShearAreaGust2 | Vspr | LidarShearV.cpp ShearArea | float | 0 | W |  | true | L | LidarShearAreaGust2 | IO.Algorithm.PitchControl
S_ShearState | Vspr | LidarShearV.cpp ShearState:1 | int | 0 | W |  | true |  | ShearState | IO.Algorithm.PitchControl
S_ShearExtraPitchRate | Vspr | LidarShearV.cpp ShearExtraPitchRate | float | 0 | W |  | true | A/T | ShearExtraPitchRate | IO.Algorithm.PitchControl
S_LidarShearpitch | Vspr | LidarShearV.cpp-Measured Mean Pitch | float | 0 | W |  | true | A | LidarShearpitch | IO.Algorithm.PitchControl
S_ShearDynamicFinePitch | Vspr | GRTDynamicFinePitch | float | 0 | W |  | true | A | GRTDynamicFinePitch | IO.Algorithm.PitchControl
S_ShearExtraTimeState | Vspr | GRTExtraTimeState | bool | false | W |  | true |  | isGustUpDetectedOff | IO.Algorithm.PitchControl
S_LidarShearV0L1H | Vspr | LidarDataProcessShearH.cpp | float | 0 | W |  | true | L/T | LidarShearV0L1H | IO.Algorithm.PitchControl
S_LidarShearV0L2H | Vspr | LidarDataProcessShearH.cpp | float | 0 | W |  | true | L/T | LidarShearV0L2H | IO.Algorithm.PitchControl
S_LidarV0LShearfliter1H | Vspr | LidarShearH.cpp LidarV0LShearfliter1 | float | 0 | W |  | true | L/T | V0L_Shear1 | IO.Algorithm.PitchControl
S_LidarV0LShearfliter2H | Vspr | LidarShearH.cpp LidarV0LShearfliter2 | float | 0 | W |  | true | L/T | V0L_Shear2 | IO.Algorithm.PitchControl
S_LidarShearAreaH | Vspr | LidarShearH.cpp ShearArea | float | 0 | W |  | true | L | LidarShearAreaH | IO.Algorithm.PitchControl
S_LidarShearAreaGust1H | Vspr | LidarShearH.cpp ShearArea | float | 0 | W |  | true | L | LidarShearAreaGust1H | IO.Algorithm.PitchControl
S_LidarShearAreaGust2H | Vspr | LidarShearH.cpp ShearArea | float | 0 | W |  | true | L | LidarShearAreaGust2H | IO.Algorithm.PitchControl
S_ShearStateH | Vspr | LidarShearH.cpp ShearState:1 | int | 0 | W |  | true |  | ShearStateH | IO.Algorithm.PitchControl
S_ShearExtraPitchRateH | Vspr | LidarShearH.cpp ShearExtraPitchRate | float | 0 | W |  | true | A/T | ShearExtraPitchRateH | IO.Algorithm.PitchControl
S_LidarShearpitchH | Vspr | LidarSheaH.cpp-Measured Mean Pitch | float | 0 | W |  | true | A | LidarShearpitchH | IO.Algorithm.PitchControl
S_ShearHDynamicFinePitch | Vspr | GRTDynamicFinePitch | float | 0 | W |  | true | A | GRTDynamicFinePitch | IO.Algorithm.PitchControl
S_ShearHExtraTimeState | Vspr | GRTExtraTimeState | bool | false | W |  | true |  | isGustUpDetectedOff | IO.Algorithm.PitchControl
S_FaultNumber | Vspr | S_FaultNumber | int | 0 | W |  | true | L/T | FaultNumber | IO.Algorithm.PitchControl
S_LidarV0LLast | Vspr | LidarV0LLast | float | 0 | W |  | true | L/T | LidarV0LLast | IO.Algorithm.PitchControl
S_SimulationCurrentTime | Vspr | Get SimulationCurrentTime For Lidar Simulation | float | 0 | W |  | true | T | SimulationCurrentTime | IO.Algorithm.PitchControl
;
S_EstimateFa | Vspr | EstimateFa | float | 0 | W |  | false |  | EstimateFa | IO.Algorithm.PitchControl
S_EstimateEffectiveWindSpeed | Vspr | EstimateEffectiveWindSpeed | float | 0 | W |  | false | L/T | EstimateEffectiveWindSpeed | IO.Algorithm.PitchControl
S_EstimateLamda | Vspr | EstimateLamda | float | 0 | W |  | false |  | EstimateLamda | IO.Algorithm.PitchControl
S_EstimateEffectiveWindSpeedFiltered | Vspr | EstimateEffectiveWindSpeedFiltered | float | 0 | W |  | false | L/T | EstimateEffectiveWindSpeedFiltered | IO.Algorithm.PitchControl
;PowerDynamicControl
S_PowerShootFlag | Vspr |  | bool | false | W |  | true |  | PowerShootFlag | IO.Algorithm.Powershoot
S_PowerShootAboveThreshold | Vspr |  | bool | false | W |  | true |  | PowerShootAboveThreshold | IO.Algorithm.Powershoot
S_PowerShootTimer | Vspr |  | float | 0 | W |  | true |  | PowerShootTimer | IO.Algorithm.Powershoot
S_PowerShootFactor | Vspr |  | float | 1.0 | W |  | true |  | PowerShootFactor | IO.Algorithm.Powershoot
;GeneratorSpeedDynamicControl
S_HighGenSpeedDynCtrlBiasFlag | Vspr | High Generator Speed Bias Flag | bool | true | W |  | true |  | HighGenSpeedDynCtrlBiasFlag | IO.Algorithm.DynGenSpeed
S_HighGenSpeedDynCtrlBiasFactor | Vspr | High Generator Speed Bias Factor | float | 0.0 | W |  | true | A/T | HighGenSpeedDynCtrlBiasFactor | IO.Algorithm.DynGenSpeed
S_HighGenSpeedDynCtrlBiasTimer | Vspr | High Generator Speed Bias Timer | float | 0 | W |  | true |  | HighGenSpeedDynCtrlBiasTimer | IO.Algorithm.DynGenSpeed
;SwOverspeedFlag | [8 empty] | wOverspeedFlag
S_SwOverspeedFlag | Vspr | S_SwOverspeedFlag | bool | false | W |  | true |  | SwOverspeedFlag | IO.Algorithm.SwOverspeedFlag
; Blade clearance test variables
S_AzimuthAngle | Vspr | S_AzimuthAngle | float | 0 | W |  | true | A | S_AzimuthAngle | IO.Algorithm.SwOverspeedFlag
S_AuxPit0 | Vspr | S_AuxPit0 | float | 0 | W |  | true | A | S_AuxPit0 | IO.Algorithm.SwOverspeedFlag
S_AuxPit1 | Vspr | S_AuxPit1 | float | 0 | W |  | true | A | S_AuxPit1 | IO.Algorithm.SwOverspeedFlag
S_AuxPit2 | Vspr | S_AuxPit2 | float | 0 | W |  | true | A | S_AuxPit2 | IO.Algorithm.SwOverspeedFlag
S_Azflag | Vspr | S_Azflag | bool | false | W |  | true |  | S_Azflag | IO.Algorithm.SwOverspeedFlag
S_PitDemand0 | Vspr | S_PitDemand0 | float | 0 | W |  | true | A | S_PitDemand0 | IO.Algorithm.SwOverspeedFlag
S_PitDemand1 | Vspr | S_PitDemand1 | float | 0 | W |  | true | A | S_PitDemand1 | IO.Algorithm.SwOverspeedFlag
S_PitDemand2 | Vspr | S_PitDemand2 | float | 0 | W |  | true | A | S_PitDemand2 | IO.Algorithm.SwOverspeedFlag
S_AuxAllowed | Vspr | S_AuxAllowed | bool | false | W |  | true |  | S_AuxAllowed | IO.Algorithm.SwOverspeedFlag
S_SecAuxAllowed | Vspr | S_SecAuxAllowed | bool | false | W |  | true |  | S_SecAuxAllowed | IO.Algorithm.SwOverspeedFlag
S_TimeSinceClearanceCtr | Vspr | S_TimeSinceClearanceCtr | float | 0.0 | W |  | true | T | S_TimeSinceClearanceCtr | IO.Algorithm.SwOverspeedFlag
S_SecondProTime | Vspr | S_SecondProTime | float | 0.0 | W |  | true | T | S_SecondProTime | IO.Algorithm.SwOverspeedFlag
S_ClearanceCtrTimes | Vspr | S_ClearanceCtrTimes | int | 0 | W |  | true |  | S_ClearanceCtrTimes | IO.Algorithm.SwOverspeedFlag
; Noise Control | [8 empty] | Noise Control
S_NoiseControlCalEnable | Vspr | Noise Control Calculation enable | bool | false | W |  | true | - | NoiseControlCalEnable
S_NoiseControlOutputEnable | Vspr | Noise Control Output enable | bool | false | W |  | true | - | NoiseControlOutputEnable
S_NoiseControlState | Vspr |  | int | 0 | W |  | true | - | NoiseControlState
S_NoiseControlSpeedSetpoint | Vspr |  | float | 0 | W |  | true | A/T | NoiseControlSpeedSetpoint
S_NoiseControlPitchMinSetpoint | Vspr |  | float | 0 | W |  | true | A | NoiseControlPitchMinSetpoint
S_NoiseControlPowerSetpoint | Vspr |  | float | 0 | W |  | true | P | NoiseControlPowerSetpoint
S_NoiseControlSpeedOverlimit | Vspr |  | int | 0 | W |  | true | - | NoiseControlSpeedOverlimit
S_NoiseControlPitchOverlimit | Vspr |  | int | 0 | W |  | true | - | NoiseControlPitchOverlimit
S_NoiseControlSubIndex | Vspr |  | int | 0 | W |  | true | - | NoiseControlSubIndex
S_NoiseControlTime | Vspr |  | float | 0 | W |  | true | T | NoiseControlTime
S_NoiseControlPitchMinSetpointCmd | Vspr |  | float | 0 | W |  | true | A | NoiseControlPitchMinSetpointCmd

## Derived
; | [10 empty] | HMI
Name | Subsystem | Description en_GB | Data Type | Initial Value | Expression | Filter Type | Time Parameter | Reset Condition | Discon Log | Dimensions | Display Name en_GB | Display Location en_GB | Display Units | Logging Config
; Life-Time
L_BuildId | Controller | The controller software build id | int | 0 |  |  |  | N
;
; Wind Conditions
D_StartupShortAverageWindSpeed | Anem | Short term average wind speed for safe start | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetStartupWindSpeedShortAvT() | W | true | L/T | Startup Short Avg Wind Speed | IO.Algorithm.Wind | m/s
D_StartupLongAverageWindSpeed | Anem | Long term average wind speed for safe start | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetStartupWindSpeedLongAvT() | W | true | L/T | Startup Long Avg Wind Speed | IO.Algorithm.Wind | m/s
D_HighYawErrorAverageWindSpeed | Anem | Average wind speed for high yaw error alarm | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetHighYawErrorWindSpeedAvT() | W | true | L/T | Avg Wind Speed For High Yaw Error Alarm | IO.Algorithm.Wind | m/s
D_CutoutWindSpeed1 | Anem | Average wind speed for high yaw error alarm | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetCutoutWindSpeedAvT1() | W | true | L/T | Avg Wind Speed For High Yaw Error Alarm | IO.Algorithm.Wind | m/s
D_CutoutWindSpeed2 | Anem | Average wind speed for high yaw error alarm | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetCutoutWindSpeedAvT2() | W | true | L/T | Avg Wind Speed For High Yaw Error Alarm | IO.Algorithm.Wind | m/s
D_HighWindPowerAverageWindSpeed | Anem | Average wind speed for generator speed limit | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetHighWindPowerLimitWindSpeedAvT() | W |  | L/T | Avg Wind Speed For Power Limit | IO.Algorithm.Wind | m/s
D_HighWindSpeedAverageWindSpeed | Anem | Average wind speed for generator speed limit | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetHighWindSpeedLimitWindSpeedAvT() | W | true | L/T | Avg Wind Speed For Power Limit | IO.Algorithm.Wind | m/s
D_StallFinePitchAverageWindSpeed | Anem | Average wind speed for Stall Fine Pitch | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetStallFinePitchWindSpeedAvT() | W | false | L/T | Avg Wind Speed For Stall | IO.Algorithm.Wind | m/s
;
; De-rating
D_RatedSpeedDownFactorSel | Vspr |  | float | 1 | S_GetTargetSpeedFactor() |  | P_GetSpeedUpgradeRateLimit()
D_DeRatedSpeed | Vspr | De-rated Speed | float | 0 | std::max(0.0f, std::min(P_GetRatedGeneratorSpeed() , CI_GetAlgSpeedSetpointLimit()) ) *D_GetSpeedUpgradeRateLimitSel()*D_GetRatedSpeedDownFactorSel() | RateLimit | P_GetSpeedSetpointRateLimit() | W |  | A/T | DeRated Speed | IO.Algorithm.DeRating | rpm
D_DeRatedPower | Vspr | De-rated Power | float | 0 | std::max(0.0f, std::min(P_GetSteadyShaftPowerLimit() , CI_GetAlgPowerSetpointLimit())) |  |  | W | true | P | DeRated Power | IO.Algorithm.DeRating | kW
;
;Nacelle Acceleration Fore-aft De-rating
D_NacAccXDeratingAvAcc | Vspr | Average measured fore-aft nacelle acceleration | float | 0 | fabs(CI_GetAlgNacelleForeAftAcceleration()) | MovAve | P_GetNacAccXDeratingAvT() | W | false | L/TT | Average measured for-aft nacelle accleration | IO.Algorithm.NacAcc | m/s^2
D_NacAccXDeratingWindSpeed | Anem | Average measured Wind Speed | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetNacAccXDeratingAvT() | W | false | L/T | Average measured wind speed | IO.Algorithm.Wind | m/s
D_NacAccXDeratingThreshold | Vspr | Fore-aft nacelle acceleration threshold | float | 0 | D_GetNacAccXDeratingWindSpeed() | LookUpTable | T_NacAccXDeratingThreshold | W | false | L/TT
;
;High Wind De-rating
D_HighWindPowerLimitFactor | Vspr | Power Limit Factor Look Up Table | float | 0 | D_GetHighWindPowerAverageWindSpeed() | LookUpTable | T_HighWindPowerLimitFactorSchedule | W |  |  | High Wind Power Limit Factor | IO.Algorithm.DeRating
D_HighWindDeratingPower | Vspr | High Wind De-rating Power | float | 0 | D_GetHighWindPowerLimitFactor()*P_GetSteadyShaftPowerLimit() |  |  | W |  |  | High Wind De-rating Power | IO.Algorithm.DeRating | kW
D_HighWindSpeedLimitFactor | Vspr | Power Limit Factor Look Up Table | float | 0 | D_GetHighWindSpeedAverageWindSpeed() | LookUpTable | T_HighWindSpeedLimitFactorSchedule | W | true |  | High Wind Power Limit Factor | IO.Algorithm.DeRating
;
; IPC
D_MaximumBladeBendingMoment | Vspr | IPC Limit | float | 0 | std::max(CI_GetAlgOutOfPlaneBendingMoment1(),std::max(CI_GetAlgOutOfPlaneBendingMoment2(),CI_GetAlgOutOfPlaneBendingMoment3())) | MovAve | P_GetIPCMinimumBladeBendingMomentMovAvTC() | W | true |  | IPC Limit | IO.Algorithm.IPC | kN.m
D_IPCAboveThresholdDuration | Vspr | D_IPCAboveThresholdDuration | float | 0 | D_GetMaximumBladeBendingMoment() > P_GetIPCMinimumBladeBendingMoment() | TrueDuration |  | W | true | T
;Startup control
D_RatedGeneratorTorque | Vspr | Torque required for rated power & speed | float | 0 | P_GetSteadyShaftPowerLimit() / P_GetRatedGeneratorSpeed() |  |  | W | true | FL | Rated Generator Torque | IO.Algorithm.Startup | kN.m
D_ShaftPowerSetpointTarget | Vspr | Setpoint target for steady state generated shaft power | float | 0 | S_GetStartupPowerFraction() * D_GetDeRatedPower() |  |  | W | true | P | Shaft Power Setpoint Target
D_ShaftPowerSetpointTargetRateLimited | Vspr | Rate Limited Setpoint target for steady state generated shaft power | float | 0 | D_GetShaftPowerSetpointTarget() | RateLimit | P_GetShaftPowerTargetRateLimit() | W | true | P | Shaft Power Setpoint Target Rate Limited | IO.Algorithm.Startup | kW
D_ShaftPowerSetpointTargetRateLimitedExt | Vspr | Rate Limited Setpoint target for steady state generated shaft power Ext | float | 0 | S_GetDeratingPowerTarget() | RateLimit | P_GetDeratingPowerRateLimit() | W | true | P | Shaft Power Setpoint Target Rate Limited | IO.Algorithm.Startup | kW
D_ShaftPowerSetpoint | Vspr | Setpoint for steady state generated shaft power | float | 0 | std::min(D_GetRatedGeneratorTorque()*D_GetDeRatedSpeed(),std::min(D_GetShaftPowerSetpointTargetRateLimited(),D_GetShaftPowerSetpointTargetRateLimitedExt())) *D_GetPowerIncreaseFactorRateLimitSel() |  |  | W | true | P | Shaft Power Setpoint | IO.Algorithm.Startup | kW
D_GeneratorTorqueProductionSetpoint | Vspr | Torque setpoint during power production | float | 0 | GetTorqueFromPowerAndSpeedLimits(D_GetShaftPowerSetpoint(),P_GetLowSpeedSyncSpeed(),D_GetDeRatedSpeed()) |  |  | W |  | FL | Generator Torque Production Setpoint | IO.Algorithm.Startup | kN.m
D_GeneratorTorqueShutdownMax | Vspr | Maximum torque during shutdowns | float | 0 | D_GetShaftPowerSetpoint() | LookUpTable | T_NormalShutdownTorque | W |  | FL | Generator Torque Shutdown Max | IO.Algorithm.Startup | kN.m
D_GeneratorTorqueShutdownSetpoint | Vspr | Torque setpoint during shutdowns | float | 0 | T_NormalShutdownTorque.Enabled() ? std::min(S_GetShutdownMaxTorque(), D_GetGeneratorTorqueShutdownMax()) : D_GetGeneratorTorqueProductionSetpoint() |  |  | W |  | FL | Generator Torque Shutdown Setpoint | IO.Algorithm.Startup | kN.m
D_GeneratorTorqueSetpoint | Vspr | Setpoint for steady state torque | float | 0 | S_GetShutdownFlag() ? D_GetGeneratorTorqueShutdownSetpoint() : D_GetGeneratorTorqueProductionSetpoint() |  |  | W | true | FL | Generator Torque Setpoint | IO.Algorithm.Startup | kN.m
D_PowerControlSpeedSetpoint | Vspr | Setpoint for steady state speed if in power production | float | 0 | D_GetGeneratorTorqueSetpoint() == 0 ? P_GetLowSpeedSyncSpeed() : D_GetShaftPowerSetpoint() / D_GetGeneratorTorqueSetpoint() |  |  | W | true | A/T | Power Control Speed Setpoint | IO.Algorithm.Startup | rpm
D_DisconnectedSpeedSetpoint | Vspr | Setpoint for steady state speed if not in power production | float | 0 | S_GetShutdownFlag() ? std::min(S_GetDisconnectedSpeedSetpointTarget(), D_GetDeRatedSpeed()) :std::min(S_GetDisconnectedSpeedSetpointTarget()+0.3f , D_GetDeRatedSpeed()) | RateLimit | P_GetSpeedSetpointRateLimit() | W | true | A/T | Disconnected Speed Setpoint | IO.Algorithm.Startup | rpm
D_GeneratorSpeedSetpoint | Vspr | Setpoint for steady state speed | float | 0 | CI_GetAlgPcsSynchronised() ? std::max(D_GetPowerControlSpeedSetpoint(),D_GetDisconnectedSpeedSetpoint()) : D_GetDisconnectedSpeedSetpoint() |  |  | W | true | A/T | Generator Speed Setpoint | IO.Algorithm.Startup | rpm
D_DurationStartUpWait | Vspr | D_DurationStartUpWait | float | 0 | (CI_GetAlgGeneratorSpeed() >P_GetStartupWaitSpeed())&&InVsprStartUpStatesFilter() | TrueDuration |  | W | true | T |  | IO.Algorithm.Startup
D_RunUpPitchAngle1 | Vspr | D_RunUpPitchAngle | float | 0 | CI_GetAlgGeneratorSpeed() | LookUpTable | T_Pitchmin1 | W | true | A |  | IO.Algorithm.Startup | deg
D_RunUpPitchAngle2 | Vspr | D_RunUpPitchAngle | float | 0 | std::max(P_GetMinimumFinePitch(),(D_GetRunUpPitchAngle2()+S_GetStartPitchRate()*P_GetControllerCycleTime())) |  |  | W | true | A |  | IO.Algorithm.Startup | deg
;
; Pitch
D_CurrentMeasuredPitchAngle123 | Pitch | Overall blade angle of all three blades | float | 0 | (CI_GetAlgPitchPosition1() + CI_GetAlgPitchPosition2() + CI_GetAlgPitchPosition3()) / 3.0f |  |  | W |  | A | Current Measured Pitch Angle 123 | IO.Algorithm.Pitch | deg
D_DurationGeneratorSpeedWithinSyncTol | Vspr | Duration the generator speed is within tolerance of sync speed | float | 0 | fabs(CI_GetAlgGeneratorSpeed() - P_GetLowSpeedSyncSpeed()) < P_GetSyncSpeedTol() | TrueDuration |  | W |  | T | Duration Gen Speed Within Sync Tolerance | IO.Algorithm.Pitch | s
D_AverageMeasuredPitchAngle | Anem | Average measured pitch angle | float | 0 | D_GetCurrentMeasuredPitchAngle123() | MovAve | P_GetGentlePitDropMeasuredPitchAvT() | W | true | A | Average Measured Pitch Angle | IO.Algorithm.Pitch | deg
D_StallFinePitch | Vspr | Fine Pitch Angle Look Up Table | float | 0 | D_GetStallFinePitchAverageWindSpeed() | LookUpTable | T_StallFinePitchSchedule | W | false |  | Stall Fine Pitch | IO.Algorithm.Pitch | deg
;
;Nacelle Accleration Fine Pitch Schedule
D_NacelleAccelerationXAverage | Vspr | Avdrage measured for-aft nacelle accleration | float | 0 | fabs(CI_GetAlgNacelleForeAftAcceleration()) | MovAve | P_GetNacAccXPitchScheduleAvT() | W | true | L/TT | Avdrage measured for-aft nacelle accleration | IO.Algorithm.NacAcc | m/s^2
D_NacAccXPitSchedWindSpeed | Anem | Average wind speed for nacelle acceleration for-aft pitch schedule | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetNacAccXPitchScheduleAvT() | W | true | L/T | Avg Wind Speed For High Yaw Error Alarm | IO.Algorithm.Wind | m/s
D_NacAccXAverageThreshold | Vspr | Nacelle acceleration for-aft threshold for trigger fine pitch schedule | float | 0 | D_GetNacAccXPitSchedWindSpeed() | LookUpTable | T_FinePitchScheduleNacAccXThreshold | W | true | L/TT
D_NacAccXAboveThresholdDuration | Vspr | D_NacAccXAboveThresholdDuration | float | 0 | D_GetNacelleAccelerationXAverage() >(D_GetNacAccXAverageThreshold()) | TrueDuration |  | W | true | T
D_NacAccXAboveThreshold | Vspr | D_NacAccXAboveThreshold | bool | false | D_GetNacAccXAboveThresholdDuration()>P_GetNacAccXAboveThresholdMinDuration() | PosEdge |  | W | true
D_NacAccXBelowThresholdDuration | Vspr | Time of nacelle acceleration for-aft value below threshold | float | 0 | D_GetNacelleAccelerationXAverage() < (D_GetNacAccXAverageThreshold()) | TrueDuration |  | W | true | T
D_NacAccXBelowThreshold | Vspr | D_NacAccXBelowThreshold | bool | false | D_GetNacAccXBelowThresholdDuration()>P_GetNacAccXBelowThresholdMinDuration() | PosEdge |  | W | true
;
;Normal Shutdown
D_NormalShutdownPitchRateLookup | Vspr | Pitch rate from normal shutdown lookup table | float | 0 | (CI_GetAlgPitchPosition1() + CI_GetAlgPitchPosition2() +CI_GetAlgPitchPosition3() )/3.0 | LookUpTable | T_NormalShutdownPitchrate | W |  | FL |  |  | kN.m
D_NormalShutdownPitchRateLookup2 | Vspr | Pitch rate from normal shutdown lookup table2 | float | 0 | CI_GetAlgGeneratorSpeed() | LookUpTable | T_NormalShutdownPitchrate2
D_NormalShutdownPitchRate | Vspr | Pitch rate demand for normal shutdown | float | 0 | (P_GetNormalShutdownMode()==0)?D_GetNormalShutdownPitchRateLookup() : D_GetNormalShutdownPitchRateLookup2() |  |  | W | true | FL | Normal Shutdown Pitch Rate | IO.Algorithm.Shutdown | kN.m
;
; Fast Shutdown
D_FastShutdownTorqueLookup | Vspr | Torque from fast shutdown lookup table | float | 0 | CI_GetAlgGeneratorSpeed() | LookUpTable | T_FastShutdownTorque | W |  | FL |  |  | kN.m
D_FastShutdownTorque | Vspr | Torque demand for fast shutdown | float | 0 | D_GetFastShutdownTorqueLookup() | RateLimit | P_GetFastShutdownTorqueRateLimit() | W | true | FL | Fast Shutdown Torque | IO.Algorithm.Shutdown | kN.m
;
; Gridloss Shutdown
D_GridLossShutdownPitchRateLookup | Vspr | Pitch rate from gridloss shutdown lookup table | float | 0 | (CI_GetAlgPitchPosition1() + CI_GetAlgPitchPosition2() +CI_GetAlgPitchPosition3() )/3.0 | LookUpTable | T_GridLossShutdownPitchRate | W |  | FL |  |  | deg
D_GridLossShutdownPitchRate | Vspr | Pitch rate demand for gridloss shutdown | float | 0 | D_GetGridLossShutdownPitchRateLookup() |  |  | W | true | FL | Gridloss Shutdown Pitch Rate | IO.Algorithm.Shutdown | deg
D_GridLossShutdownTorqueLookup | Vspr | Torque from gridloss shutdown lookup table | float | 0 | S_GetVsprStateCounter() | LookUpTable | T_GridLossShutdownTorque | W |  | FL |  |  | kN.m
D_GridLossShutdownTorque | Vspr | Torque demand for gridloss shutdown | float | 0 | std::min(S_GetShutdownMaxTorque(), D_GetGridLossShutdownTorqueLookup()) |  |  | W | true | FL | Grid Loss Shutdown Torque | IO.Algorithm.Shutdown | kN.m
;
; Startup Pitch Schedule
D_MeasuredTipSpeedRatio | Vspr | Measured Tip Speed Ratio | float | 0.00 | CI_GetAlgGeneratorSpeed()/P_GetGearboxRatio()*P_GetRotorRadius() / std::max(D_GetStartupShortAverageWindSpeed(),1.0f) |  |  | W |  |  | Measured Tip Speed Ratio | IO.Algorithm.Pitch
D_TAverageTipSpeedRatio | Vspr | Average Tip Speed Ratio | float | 0.00 | D_GetMeasuredTipSpeedRatio() | MovAve | P_GetTipSpeedRatioAvT() | W |  |  | Average Tip Speed Ratio | IO.Algorithm.Pitch
D_StartupPitchWindValue | Vspr | Startup pitch schedule on wind speed | float | 0.00 | std::max(D_GetStartupShortAverageWindSpeed(),D_GetStartupLongAverageWindSpeed()) | LookUpTable | T_StartupPitchWindSchedule | W |  | A |  |  | deg
D_StartupPitchTSRValue | Vspr | Startup pitch schedule on tip speed ratio | float | 0.00 | D_GetTAverageTipSpeedRatio() | LookUpTable | T_StartupPitchTSRSchedule | W |  | A |  |  | deg
D_StartupPitchWind | Vspr | Startup pitch schedule on wind speed | float | 0.00 | T_StartupPitchWindSchedule.Enabled() ? D_GetStartupPitchWindValue() : P_GetMinimumFinePitch() |  |  | W |  | A | Startup Pitch Wind | IO.Algorithm.Pitch | deg
D_StartupPitchTSR | Vspr | Startup pitch schedule on tip speed ratio | float | 0.00 | T_StartupPitchTSRSchedule.Enabled() ? D_GetStartupPitchTSRValue() : P_GetMinimumFinePitch() |  |  | W |  | A | Startup Pitch TSR | IO.Algorithm.Pitch | deg
D_StartupPitchAngle | Vspr | Startup Pitch Angle | float | 0.00 | std::max(D_GetStartupPitchWind(),D_GetStartupPitchTSR()) |  |  | W |  | A | Startup Pitch Angle | IO.Algorithm.Pitch | deg
;
; Alarm Edges
D_EstimatedMeanPitchRate | Vspr | D_EstimatedMeanPitchRate | float | 0 | (D_GetEstimatedPitchRate1()+D_GetEstimatedPitchRate2()+D_GetEstimatedPitchRate3() )/3 |  |  |  | true
D_SustainedSwOverspeedDuration | Vspr | Duration of a software overspeed | float | 0 | ( CI_GetAlgGeneratorSpeed() > P_GetMaxGeneratorSpeedForSwTrip() ) && ( D_GetEstimatedMeanPitchRate() > P_GetSustainedSwOverspeedPitchrate() ) | TrueDuration |  | W | true | T | Overspeed Duration | IO.Algorithm.Alarm | s
D_SwOverspeedDuration | Vspr | Duration of a software overspeed | float | 0 | (CI_GetAlgGeneratorSpeed() > P_GetMaxGeneratorSpeedForSwTrip())&& ( D_GetEstimatedMeanPitchRate()< P_GetSustainedSwOverspeedPitchrate() ) | TrueDuration |  | W | true | T | Overspeed Duration | IO.Algorithm.Alarm | s
D_FollowingError1 | Pitch | Pitch following error for blade 1 | float | 0 | CO_GetAlgPitchPositionDemand1() - CI_GetAlgPitchPosition1() |  |  | W | true | A | Following Error 1 | IO.Algorithm.Alarm | deg
D_FollowingError2 | Pitch | Pitch following error for blade 2 | float | 0 | CO_GetAlgPitchPositionDemand2() - CI_GetAlgPitchPosition2() |  |  | W | true | A | Following Error 2 | IO.Algorithm.Alarm | deg
D_FollowingError3 | Pitch | Pitch following error for blade 3 | float | 0 | CO_GetAlgPitchPositionDemand3() - CI_GetAlgPitchPosition3() |  |  | W | true | A | Following Error 3 | IO.Algorithm.Alarm | deg
D_FollowingErrorDuration1 | Pitch | Time above threshold of pitch following error 1 | float | 0 | (float) fabs(D_GetFollowingError1()) > P_GetMaximumPitchFollowingError() && CI_GetAlgPitchPosition1() < P_GetMaxPitchForFollowingError() | TrueDuration |  | W | true | T | Following Error High 1 | IO.Algorithm.Alarm
D_FollowingErrorDuration2 | Pitch | Time above threshold of pitch following error 2 | float | 0 | (float) fabs(D_GetFollowingError2()) > P_GetMaximumPitchFollowingError() && CI_GetAlgPitchPosition2() < P_GetMaxPitchForFollowingError() | TrueDuration |  | W | true | T | Following Error High 2 | IO.Algorithm.Alarm
D_FollowingErrorDuration3 | Pitch | Time above threshold of pitch following error 3 | float | 0 | (float) fabs(D_GetFollowingError3()) > P_GetMaximumPitchFollowingError() && CI_GetAlgPitchPosition3() < P_GetMaxPitchForFollowingError() | TrueDuration |  | W | true | T | Following Error High 3 | IO.Algorithm.Alarm
D_MeanPitchPositionDemand | Pitch | Pitch Position demand, mean of three blades | float | 0 | (CO_GetAlgPitchPositionDemand1()+CO_GetAlgPitchPositionDemand2()+CO_GetAlgPitchPositionDemand3())/3 |  |  | W | true | A | Mean Pitch Position Demand | IO.Algorithm.Alarm | deg
D_PitchDemandRate | Pitch | Pitch demand difference | float | 0 | D_GetMeanPitchPositionDemand() | RateOfChange | 0.2f | W | true | A/T | Pitch Demand Rate | IO.Algorithm.Alarm | deg/s
D_IpcDemandError | Pitch | IPC Demand Error | float | 0 | D_GetMeanPitchPositionDemand() - S_GetVsprPitchDemand() |  |  | W | true | A | IPC Demand Error | IO.Algorithm.Alarm | deg
D_PitchPositionDifference12 | Pitch | Difference between pitch demands of blade 1 and 2 | float | 0 | (float) fabs(CI_GetAlgPitchPosition1() - CI_GetAlgPitchPosition2()) |  |  | W |  | A | Pitch Demand Difference 12 | IO.Algorithm.Alarm | deg
D_PitchPositionDifference23 | Pitch | Difference between pitch demands of blade 2 and 3 | float | 0 | (float) fabs(CI_GetAlgPitchPosition2() - CI_GetAlgPitchPosition3()) |  |  | W |  | A | Pitch Demand Difference 23 | IO.Algorithm.Alarm | deg
D_PitchPositionDifference13 | Pitch | Difference between pitch demands of blade 1 and 3 | float | 0 | (float) fabs(CI_GetAlgPitchPosition1() - CI_GetAlgPitchPosition3()) |  |  | W |  | A | Pitch Demand Difference 13 | IO.Algorithm.Alarm | deg
D_PitchDemandDifference12 | Pitch | Difference between pitch demands of blade 1 and 2 | float | 0 | (float) fabs(CO_GetAlgPitchPositionDemand1() - CO_GetAlgPitchPositionDemand2()) |  |  | W |  | A | Pitch Demand Difference 12 | IO.Algorithm.Alarm | deg
D_PitchDemandDifference23 | Pitch | Difference between pitch demands of blade 2 and 3 | float | 0 | (float) fabs(CO_GetAlgPitchPositionDemand2() - CO_GetAlgPitchPositionDemand3()) |  |  | W |  | A | Pitch Demand Difference 23 | IO.Algorithm.Alarm | deg
D_PitchDemandDifference13 | Pitch | Difference between pitch demands of blade 1 and 3 | float | 0 | (float) fabs(CO_GetAlgPitchPositionDemand1() - CO_GetAlgPitchPositionDemand3()) |  |  | W |  | A | Pitch Demand Difference 13 | IO.Algorithm.Alarm | deg
D_EstimatedPitchRate1 | Pitch | Pitch estimated pitch rate 1 | float | 0 | CI_GetAlgPitchPosition1() | RateOfChange | 0.1f | W | true | A/T | Estimated Pitch Rate 1 | IO.Algorithm.Alarm | deg/s
D_EstimatedPitchRate2 | Pitch | Pitch estimated pitch rate 2 | float | 0 | CI_GetAlgPitchPosition2() | RateOfChange | 0.1f | W | true | A/T | Estimated Pitch Rate 2 | IO.Algorithm.Alarm | deg/s
D_EstimatedPitchRate3 | Pitch | Pitch estimated pitch rate 3 | float | 0 | CI_GetAlgPitchPosition3() | RateOfChange | 0.1f | W | true | A/T | Estimated Pitch Rate 3 | IO.Algorithm.Alarm | deg/s
D_FollowingErrorRate1 | Pitch | Pitch rate following error for blade 1 | float | 0 | CO_GetAlgPitchRateDemand1() - D_GetEstimatedPitchRate1() |  |  | W | true | A | Following Error Rate 1 | IO.Algorithm.Alarm | deg/s
D_FollowingErrorRate2 | Pitch | Pitch rate following error for blade 2 | float | 0 | CO_GetAlgPitchRateDemand2() - D_GetEstimatedPitchRate2() |  |  | W | true | A | Following Error Rate 2 | IO.Algorithm.Alarm | deg/s
D_FollowingErrorRate3 | Pitch | Pitch rate following error for blade 3 | float | 0 | CO_GetAlgPitchRateDemand3() - D_GetEstimatedPitchRate3() |  |  | W | true | A | Following Error Rate 3 | IO.Algorithm.Alarm | deg/s
D_FollowingErrorRateDuration1 | Pitch | Time above threshold of pitch following error rate 1 | float | 0 | (float) fabs(D_GetFollowingErrorRate1()) > P_GetMaximumPitchFollowingErrorRate() && CI_GetAlgPitchPosition1() < P_GetMaxPitchForFollowingError() | TrueDuration |  | W | true | T | Following Error Rate High 1 | IO.Algorithm.Alarm
D_FollowingErrorRateDuration2 | Pitch | Time above threshold of pitch following error rate 2 | float | 0 | (float) fabs(D_GetFollowingErrorRate2()) > P_GetMaximumPitchFollowingErrorRate() && CI_GetAlgPitchPosition2() < P_GetMaxPitchForFollowingError() | TrueDuration |  | W | true | T | Following Error Rate High 2 | IO.Algorithm.Alarm
D_FollowingErrorRateDuration3 | Pitch | Time above threshold of pitch following error rate 3 | float | 0 | (float) fabs(D_GetFollowingErrorRate3()) > P_GetMaximumPitchFollowingErrorRate() && CI_GetAlgPitchPosition3() < P_GetMaxPitchForFollowingError() | TrueDuration |  | W | true | T | Following Error Rate High 3 | IO.Algorithm.Alarm
D_EstimatedGeneratorAcceleration | Pcs | Estimated Generator acceleration | float | 0 | CI_GetAlgGeneratorSpeed() | RateOfChange | P_GetEstimatedGenAccAvt() | W | true | A/TT | Estimated Gen Acceleration | IO.Algorithm.Alarm | rpm
D_FilterEstimatedGeneratorAcceleration | Pcs | Filter Estimated Generator acceleration | float | 0 | D_GetEstimatedGeneratorAcceleration() | MovAve | 1.0f | W | true | A/TT | Filter Estimated Gen Acceleration | IO.Algorithm.Alarm | rpm
D_EstimatedGeneratorAccAcc | Pcs | Estimated Generator acceleration | float | 0 | D_GetEstimatedGeneratorAcceleration() | RateOfChange | 2.0f | W | true | A/TT | Estimated Gen Acceleration | IO.Algorithm.Alarm | rpm
D_HighYawErrorAverageYawError | Yaw | Average yaw error signal for high yaw error alarm | float | 0 | CI_GetAlgYawError() | DirectionAverage | P_GetHighYawErrorYawAvT() | W | true | A | High Yaw Error Avg Yaw Error | IO.Algorithm.Alarm | deg
D_HighYawErrorThreshold | Yaw | Yaw Error Trip Look Up Table | float | 0 | D_GetHighYawErrorAverageWindSpeed() | LookUpTable | T_HighYawErrorThresholdSchedule | W | true | A | High Yaw Error Threshold | IO.Algorithm.Alarm | deg
D_NacelleAccelerationForeaft | Vspr | Filtered Fore-aft Nacelle Acceleration? | float | 0 | CI_GetAlgNacelleForeAftAcceleration() | MovAve | P_GetNacelleAccelerationAvT() | W | true |  | Filtered Fore-aft Nacelle Acceleration? | IO.Algorithm.Alarm | m/s^2
D_NacelleAccelerationSideside | Vspr | Filtered Side-side? Nacelle Acceleration? | float | 0 | CI_GetAlgNacelleSideSideAcceleration() | MovAve | P_GetNacelleAccelerationAvT() | W | true |  | Filtered Side-Side Nacelle Acceleration | IO.Algorithm.Alarm | m/s^2
D_NacelleAccelerationEffectiveValue | Vspr | Nacelle acceleration effective value | float | 0 | sqrt(D_GetNacelleAccelerationForeaft()*D_GetNacelleAccelerationForeaft()+D_GetNacelleAccelerationSideside()*D_GetNacelleAccelerationSideside()) |  |  | W | true |  | Nacelle acceleration effective value | IO.Algorithm.Alarm | m/s^2
;
;NonLinear stuff
D_NonLinearPitchActionTriggered | Pitch |  | bool | false | S_GetVsprNonLinearextraPitchRate() | PosEdge |  | W | true |  |  | IO.Algorithm.Alarm
D_HighYawErrorAverageForYawPitchKick | Pitch |  | float | 0 | CI_GetAlgYawError() | DirectionAverage | P_GetYawErrorMovAvTC() | W | false | A | HighYawErrorAverageForYawPitchKick | IO.Algorithm.Alarm | deg
D_LongAverageWindSpeedForYawPitchKick | Anem | Long time Average wind speed for Yaw Pitch Kick | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetYawPitchKickWindSpeedMovAvTCLong() | W | false | L/T | Long time Average wind speed for Yaw Pitch Kick | IO.Algorithm.Wind | m/s
D_ShortAverageWindSpeedForYawPitchKick | Anem | Short time Average wind speed for Yaw Pitch Kick | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetYawPitchKickWindSpeedMovAvTCShort() | W | false | L/T | Short time Average wind speed for Yaw Pitch Kick | IO.Algorithm.Wind | m/s
D_GustWindForYawPitchKick | Anem | Gust wind Calculation for Yaw Pitch Kick | float | 0 | D_GetShortAverageWindSpeedForYawPitchKick()-D_GetLongAverageWindSpeedForYawPitchKick() |  |  | W | false | L/T | Gust Wind Calculation for Yaw Pitch Kick | IO.Algorithm.Wind | m/s
;
; LVRT
D_LvrtPitchKickRate | Vspr | Minimum pitch rate during LVRT | float | 0 | D_GetCurrentMeasuredPitchAngle123() | LookUpTable | T_LvrtPitchKickRate | W | false | A/T | LVRT Pitch Kick Rate | IO.Algorithm.LVRT | deg/s
;
; Timing Performance
D_ShortAverageMeasuredCycleTime | Monitor | Short-averaged measured controller cycle time | float | 0 | S_GetMeasuredControllerCycleTime() | MovAve | 1.0f | W |  |  | Short Averaged Controller Cycle Time | IO.Algorithm.Perf | s
D_LongAverageMeasuredCycleTime | Monitor | Long-averaged measured controller cycle time | float | 0 | S_GetMeasuredControllerCycleTime() | MovAve | 10.0f | W |  |  | Long Averaged Controller Cycle Time | IO.Algorithm.Perf | s
;
; Feedforward Control
D_GRTThreshold | Vspr | GRTGustArea Threshold at different V0LMovAv | float | 0 | S_GetLidarV0LMovAvNstep() | LookUpTable | T_GRTThreshold | W | true | L |  |  | kN.m
D_GRTPitchKickLookUp | Vspr | GRTPitchKick | float | 0 | S_GetLidarGustArea() | LookUpTable | T_GRTPitchKick | W | true | FL |  |  | kN.m
D_ShearPitchKick1 | Vspr | ShearPitchKick1 | float | 0 | S_GetLidarShearArea() | LookUpTable | T_ShearPitchKickThreshold1 | W | true | FL |  |  | kN.m
D_ShearPitchKick2 | Vspr | ShearPitchKick2 | float | 0 | S_GetLidarShearArea() | LookUpTable | T_ShearPitchKickThreshold2 | W | true | FL |  |  | kN.m
D_ShearPitchKickH1 | Vspr | ShearPitchKickH1 | float | 0 | S_GetLidarShearAreaH() | LookUpTable | T_ShearPitchKickHThreshold1 | W | true | FL |  |  | kN.m
D_ShearPitchKickH2 | Vspr | ShearPitchKickH2 | float | 0 | S_GetLidarShearAreaH() | LookUpTable | T_ShearPitchKickHThreshold2 | W | true | FL |  |  | kN.m
D_DthetaDv0LookUp | Vspr | DthetaDvo | float | 0 | S_GetLidarV0LBuffer() | LookUpTable | T_WsDthetaDv0 | W | true | FL |  |  | kN.m
D_DthetaDv0Limit | Vspr | DthetaDv0Limit | float | 0 | std::max(0.0f, std::min(D_GetDthetaDv0LookUp() , P_GetDthetaDvMax())) |  |  | W | true | FL | Grid Loss Shutdown Torque | IO.Algorithm.Shutdown | kN.m
D_FFExtraPitchRate | Vspr | FFExtraPitchRate | float | 0 | S_GetLidarV0LBufferDot() * D_GetDthetaDv0Limit() |  |  | W | true | A/T | Grid Loss Shutdown Torque | IO.Algorithm.Shutdown | kN.m
D_GRTExtraPitchRate | Vspr | GRTPitchKick Pitchrate RateLimit | float | 0 | S_GetGRTExtraPitchRate() | RateLimit | P_GetGRTandShearRateLimit() | W | true | A/T | GRT Extra pitch Rate Limit | IO.Algorithm.PowerShoot
D_ShearExtraPitchRate | Vspr | ShearVPitchKick Pitchrate Rate Limit | float | 0 | S_GetShearExtraPitchRate() | RateLimit | P_GetGRTandShearRateLimit() | W | true | A/T | ShearV Extra pitch Rate Limit | IO.Algorithm.PowerShoot
D_ShearExtraPitchRateH | Vspr | ShearHPitchKick Pitchrate Rate Limit | float | 0 | S_GetShearExtraPitchRateH() | RateLimit | P_GetGRTandShearRateLimit() | W | true | A/T | ShearV Extra pitch Rate Limit | IO.Algorithm.PowerShoot
;
;Estimate Wind Speed
D_GeneratorSpeedAvtForEews | Vspr | Average generator speed for EewsCal | float | 0 | CI_GetAlgGeneratorSpeed() | MovAve | P_GetGeneratorSpeedAvt() | W | false | A/T | Average generator speed for EewsCal | IO.Algorithm.Wind | m/s
D_LidarV0LRate | Vspr | Change Rate of Lidar wind speed | float | 0 | S_GetLidarV0LLast() | RateOfChange | 0.2f | W | false | A/T | Lidar wind change rate | IO.Algorithm.Wind | m/s^2
D_LidarMeasureWindFaultDuration | Vspr | Duration of Eews error | float | 0 | fabs(D_GetLidarV0LRate())<0.0003 | TrueDuration |  | W | false | A/T | Lidar error time duration | IO.Algorithm.Wind | s
;GentlePitchDrop
D_GentlePitchDropAngleMarginLimit | Vspr | Pitch drop angle margin limit look up table | float | 0 | D_GetAverageMeasuredPitchAngle() | LookUpTable | T_GentlePitchDropSchedule | W | false | A | Gentle Pitch Drop Angle Margin Limit | IO.Algorithm.GentlePitch | deg
D_GentlePitchDropAngleLimit | Vspr | Pitch drop angle margin limit look up table | float | 0 | D_GetAverageMeasuredPitchAngle()-D_GetGentlePitchDropAngleMarginLimit() |  |  | W | false | A | Gentle Pitch Drop Angle Limit | IO.Algorithm.GentlePitch | deg
;PowerDynamicControl
D_PowerShootFactorRateLimit | Vspr | Power Shoot Factor Rate Limit | float | 1.0 | S_GetPowerShootFactor() | RateLimit | 0.004 | W | true |  | Power Shoot factor Rate Limit | IO.Algorithm.PowerShoot
;GeneratorSpeedDynamicControl
D_HighGenSpeedDynCtrlBias | Vspr | High Generator Speed Bias | float | 0.0 | S_GetHighGenSpeedDynCtrlBiasFactor()*P_GetRatedGeneratorSpeed() | RateLimit | P_GetHighGenSpeedDynCtrlBiasRateLimit() | W | true | A/T | Power Shoot factor Rate Limit | IO.Algorithm.DynGenSpeed
;额定转速在过渡段提升
D_AveragePitch | Vspr |  | float | 0 | ( CI_GetAlgPitchPosition1() + CI_GetAlgPitchPosition2() + CI_GetAlgPitchPosition3() ) / 3 | MovAve | P_GetAveragePitchAvT() | W | true | A |  |  | kW
D_SpeedUpgrade | Vspr |  | float | 1 | D_GetAveragePitch() | LookUpTable | T_SpeedUpgradeInStageIII | W
D_SpeedUpgradeRateLimit | Vspr |  | float | 1 | D_GetSpeedUpgrade() | RateLimit | P_GetSpeedUpgradeRateLimit() | W
D_SpeedUpgradeRateLimitSel | Vspr |  | float | 1 | T_SpeedUpgradeInStageIII.Enabled()?D_GetSpeedUpgradeRateLimit():1.0f |  |  | W
;部分风速段额定功率提升
D_AverageWindSpeed | Vspr |  | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetAverageWindSpeedAvT() | W | true | P |  |  | kW
D_PowerIncreaseFactor | Vspr |  | float | 1 | D_GetAverageWindSpeed() | LookUpTable | T_PowerIncreaseFactorSchedule | W | true
D_PowerIncreaseFactorRateLimit | Vspr |  | float | 1 | D_GetPowerIncreaseFactor() | RateLimit | P_GetPowerIncreaseFactorRateLimit() | W | true
D_PowerIncreaseFactorRateLimitSel | Vspr |  | float | 1 | T_PowerIncreaseFactorSchedule.Enabled()&&(CI_GetAlgPowerSetpointLimit()> P_GetSteadyShaftPowerLimit()*0.85) ?D_GetPowerIncreaseFactorRateLimit():1.0f |  |  | W
;NoiseControl
D_NoiseControlRotorSpeedAverageShort | Vspr | rotor speed for noise control | float | 0 | CI_GetAlgGeneratorSpeed() | MovAve | P_GetNoiseControlSpeedMoveAverageTimeShort() | W | true | A/T
D_NoiseControlWindSpeedAverageShort | Vspr | wind speed for noise control | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetNoiseControlWindMoveAverageTimeShort() | W | true | L/T
D_NoiseControlWindSpeedAverageLong | Vspr | wind speed for noise control | float | 0 | CI_GetAlgAverageWindSpeed() | MovAve | P_GetNoiseControlWindMoveAverageTimeShort() | W | true | L/T

## Param
; | [13 empty] | HMI
Name | Subsystem | Description en_GB | Data Type | Min | Max | Alarm Consequence | Alarm Category | Initial Value | ;Check | ;Initial Value | ;Initial Value | Reset Condition | ;Algorithm Design Notes | Display Name eb_GB | Display Location eb_GB | Display Units | Display View Level | Display Change Level
; Headline Turbine Parameters
; Power Production Limits
P_RatedGeneratorSpeed | Vspr | Rated generator speed | float | 0 | 300 |  |  | 1.2357 | √ | 1.1205 | 0 | C |  | RatedGeneratorSpeed | Param.Algorithm.PowProd | rpm | Observer | Administrator
P_ShaftPowerTargetRateLimit | Vspr | Maximum rate of change for the steady state shaft power setpoint | float | 0 | 4000000 |  |  | 55000 | √ | 225000 | 0 | C | Steady Power Limit devided by startup time. Startup time should be 20-40s, longer for larger turbines | ShaftPowerTargetRateLimit | Param.Algorithm.PowProd | kW | Observer | Administrator
P_SteadyShaftPowerLimit | Vspr | Steady state shaft power limit from which speed and torque setpoints will be derived - should be P_RatedGeneratorSpeed * Rated generator torque | float | 0 | 4000000 |  |  | 2760553.5 | √ | 6790200 | 0 | C | Power at airgap, normally larger than the headline power due to electrical losses | SteadyShaftPowerLimit | Param.Algorithm.PowProd | kW | Observer | Administrator
P_MinimumFinePitch | Pitch | Minimum operable pitch angle for the collective pitch controller | float | 0 | 2 |  |  | 0 | √ | 0 | 0 | C |  | MinimumFinePitch | Param.Algorithm.PowProd | deg | Observer | Administrator
P_PositiveFeatherAngle | Pitch | Positive feather pitch angle | float | 0 | 2 |  |  | 1.5534 | √ | 1.5708 | 1.5708 | C |  | PositiveFeatherAngle | Param.Algorithm.PowProd | deg | Observer | Administrator
P_MinimumPitchRateLimit | Pitch | Minimum pitch rate limit during power production | float | -2 | 0 |  |  | -0.0694 | √ | -0.139626 | 0 | C | Limits on collective pitch control algorithm. IPC pitch rated are additional | MinimumPitchRateLimit | Param.Algorithm.PowProd | deg/s | Observer | Administrator
P_MaximumPitchRateLimit | Pitch | Maximum pitch rate limit during power production | float | 0 | 2 |  |  | 0.10472 | √ | 0.139626 | 0 | C |  | MaximumPitchRateLimit | Param.Algorithm.PowProd | deg/s | Observer | Administrator
;
;Yaw Error De-rating
P_DeratingPowerRateLimit | Vspr | Maximum power rate limit when de-rating | float | 0 | 1E8 |  |  | 30000 |  | 200000 | 200000 | C |  | Yaw Error De-rating Power Rate Limit | Param.Algorithm.Derating |  | Observer | Administrator
P_YawErrorDeratingEnable | Vspr | Power limit enabled when yaw error threshold be triggered | bool | false | true |  |  | true | √ | true | true | C |  | Yaw Error De-rating Enable | Param.Algorithm.Derating |  | Observer | Administrator
P_YawErrorDeratingPower | Vspr | Maximum power level when de-rating | float | 0 | 1E8 |  |  | 2200000 | √ | 4000000 | 4000000 | C |  | Yaw Error De-rating Power | Param.Algorithm.Derating |  | Observer | Administrator
P_YawErrorDeratingTime | Vspr | Maximum de-rating time | float | 0 | 1E8 |  |  | 300 | √ | 60 | 60 | C |  | Yaw Error De-rating Time | Param.Algorithm.Derating |  | Observer | Administrator
P_YawErrorDeratingDecreasedFactor | Vspr | Yaw error threshold decreased factor, | float | 0 | 1 |  |  | 1 |  | 1 | 1 | C |  | Yaw error threshold decreased factor | Param.Algorithm.Derating |  | Observer | Administrator
;
;Turbulence De-rating
P_NacAccXDeratingEnable | Vspr | Nacelle acceleration fore-aft de-rating switch | bool | false | true |  |  | false | √ | true | true | C |  | Nacelle Acceleration Fore-aft De-rating Enable | Param.Algorithm.Derating |  | Observer | Administrator
P_NacAccXDeratingPower | Vspr | Maximum power level when de-rating | float | 0 | 1E8 |  |  | 3000000 | √ | 4000000 | 4000000 | C |  | Nacelle Acceleration Fore-aft De-rating Power | Param.Algorithm.Derating | W | Observer | Administrator
P_NacAccXDeratingTime | Vspr | Maximum de-rating time | float | 0 | 1E8 |  |  | 180 | √ | 60 | 60 | C |  | Nacelle Acceleration Fore-aft De-rating Time | Param.Algorithm.Derating | s | Observer | Administrator
P_NacAccXDeratingAvT | Vspr | Average time constant for fore-aft nacelle acceleration | float | 0 | 1E8 |  |  | 30 | √ | 30 | 30 | C |  | Nacelle accleration for-aft value averaging time | Param.Algorithm.Derating | s | Observer | Administrator
P_TurDeratingEnabled | Vspr | Turbulence control enabled | bool | false | true |  |  | false |  | false | false | C |  | Turbulence De-rating Enabled | Param.Algorithm.TurDerating |  | Observer | Administrator
P_TurDeratingGenSpeedSafeFactor | Vspr | Generator speed safe factor | float | 0 | 300 |  |  | 1.2 |  | 1.05 | 1.05 | C |  | Turbulence De-rating Safe Speed | Param.Algorithm.TurDerating |  | Observer | Administrator
P_TurDeratingGenSpeedSafeCount | Vspr | Generator speed safe count | int | 0 | 100 |  |  | 4 |  | 4 | 4 | C |  | Turbulence De-rating Safe Count | Param.Algorithm.TurDerating |  | Observer | Administrator
P_TurDeratingPower | Vspr | Maximum shaft power level when de-rating | float | 0 | 1E8 |  |  | 2000000 |  | 2000000 | 2000000 | C |  | Turbulence De-rating Power | Param.Algorithm.TurDerating |  | Observer | Administrator
P_TurDeratingTime | Vspr | Maximum de-rating time | float | 0 | 1E8 |  |  | 600 |  | 600 | 600 | C |  | Turbulence De-rating Time | Param.Algorithm.TurDerating | s | Observer | Administrator
P_TurDeratingStepMultiplier | Vspr | Tur derating loop timestep multiplier | int | 1 | 100 |  |  | 50 |  | 50 | 50 | C |  | Turbulence De-rating Step Multiplier | Param.Algorithm.TurDerating |  | Observer | Administrator
P_HighWindPowerLimitWindSpeedAvT | Vspr | Average time constant for wind speed signal used in power limit | float | 0 | 1000 |  |  | 50 |  | 50 | 05 | C |  | HighWindPowerLimitWindSpeedAvT | Param.Algorithm.Derating | s | Observer | Administrator
P_HighWindSpeedLimitWindSpeedAvT | Vspr | Average time constant for wind speed signal used in power limit | float | 0 | 1000 |  |  | 50 |  | 50 | 05 | C |  | HighWindPowerLimitWindSpeedAvT | Param.Algorithm.Derating | s | Observer | Administrator
;
; Startup
P_StartupMinimumPitchRateLimit | Vspr | Minimum pitch rate limit during startup | float | -2 | 0 |  |  | -0.03491 | √ | -0.03491 | 0 | C |  | StartupMinimumPitchRateLimit | Param.Algorithm.Startup | deg/s | Observer | Administrator
P_LowSpeedSyncSpeed | Vspr | Generator grid synchronisation speed | float | 0 | 200 |  |  | 0.6283 | √ | 0.419 | 0 | C | Minimum speed for power production | LowSpeedSyncSpeed | Param.Algorithm.Startup | rpm | Observer | Administrator
P_SpeedSetpointRateLimit | Vspr | Maximum rate of change for the speed setpoint | float | 0 | 100 |  |  | 0.1 | √ | 0.1 | 1E10 | C | Only used for de-rating and during startup before gen connection. Normally approx rated speed divided by 100 | SpeedSetpointRateLimit | Param.Algorithm.Startup | rpm | Observer | Administrator
P_StartupWindSpeedShortAvT | Vspr | Short term averaging time constant for wind speed signal used for startup | float | 0 | 100 |  |  | 2 | √ | 2 | 2 | C |  | StartupWindSpeedShortAvT | Param.Algorithm.Startup | s | Observer | Administrator
P_StartupWindSpeedLongAvT | Vspr | Long term averaging time constant for wind speed signal used for startup | float | 0 | 100 |  |  | 15 | √ | 15 | 15 | C |  | StartupWindSpeedLongAvT | Param.Algorithm.Startup | s | Observer | Administrator
P_TipSpeedRatioAvT | Vspr | Averaging time constant for tip speed ratio signal used for startup | float | 0 | 100 |  |  | 3 | √ | 3 | 3 | C |  | TipSpeedRatioAvT | Param.Algorithm.Startup | s | Observer | Administrator
P_StartupWaitPitchangle | Vspr | P_StartupWaitPitchangle | float | 0 | 2 |  |  | 0.873 |  | 1.0472 | 1.0472 | C |  | StartupWaitPitchangle | Param.Algorithm.Startup | deg | Observer | Administrator
P_StartupWaitTime | Vspr | P_StartupWaitTime | float | 0 | 100 |  |  | 20 |  | 20 | 20 | C |  | StartupWaitTime | Param.Algorithm.Startup | s | Observer | Administrator
P_StartupWaitSpeed | Vspr | P_StartupWaitSpeed | float | 0 | 100 |  |  | 0.0471 |  | 0.058 | 0.058 | C |  | StartupWaitSpeed | Param.Algorithm.Startup | rpm | Observer | Administrator
P_RunupMinimumPitchRateLimit | Vspr | Minimum pitch rate limit during runup | float | -2 | 0 |  |  | -0.0227 |  | -0.01745 | -0.01745 | C |  | RunupMinimumPitchRateLimit | Param.Algorithm.Startup | deg/s | Observer | Administrator
P_PowerMinimumPitchRateLimit | Vspr | Minimum pitch rate limit during power | float | -2 | 0 |  |  | -0.00873 |  | -0.00873 | -0.00873 | C |  | RunupMinimumPitchRateLimit | Param.Algorithm.Startup | deg/s | Observer | Administrator
;P_StartupGspeedsetTargetRateLimit | Vspr | P_StartupGspeedsetTargetRateLimit | float | 0 | 1 |  |  | 0.042 |  | 0.042 | 0.042 | C |  | RunupMinimumPitchRateLimit | Param.Algorithm.Startup | rpm | Observer | Administrator
;P_StartupHwindGenerator | Vspr | P_StartupHwindGenerator | float | 0 | 100 |  |  | 0.576 |  | 0.576 | 0.576 | C |  | StartupWaitSpeed | Param.Algorithm.Startup | rpm | Observer | Administrator
;
; Low Wind Speed
P_LowWindSpeedModeMinDuration | Vspr | Minimum duration of the Low Wind Speed Mode | float | 0 | 10000 |  |  | 60 | √ | 60 | 60 | C | Guarantees some histeresis in switching the PCS on/off due to low wind speed mode | LowWindSpeedModeMinDuration | Param.Algorithm.LowWind |  | Observer | Administrator
P_LowWindSpeedGenSpeed | Vspr | Speed setpoint in low wind speed mode | float | 0 | 300 |  |  | 0.6283 | √ | 0.419 | 0 | C | Can be the same as the low speed sync speed unless there is a frequency clash to avoid | LowWindSpeedGenSpeed | Param.Algorithm.LowWind |  | Observer | Administrator
;
; Shutdown Parameters
P_ShutdownMaxPower | Vspr | Power level at which the grid can be disconnected from the generator | float | 0 | 4000000 |  |  | 35000 | √ | 35000 | 35000 | C |  | ShutdownMaxPower | Param.Algorithm.Shutdown |  | Observer | Administrator
P_NormalShutdownPitchRateLimitEnable | Vspr |  | bool | false | true |  |  | true
P_SemiNormalShutdownEnable | Vspr | Enable Flag | bool | false | true |  |  | true | false | false |  | C
P_NormalShutdownPitchRateLowerLimit | Vspr | Lower Pitch rate limit | float | 0 | 2 |  |  | 0.0 | 0.0698 | 0.0698 |  | C
P_NormalShutdownMode | Vspr | NormalShutdownMode | int | 0 | 2 |  |  | 0 | 0 | 0 |  | C |  | NormalShutdownMode
P_NormalShutdownPitchRate | Vspr | Open-loop pitch rate for normal shutdown after disconnection | float | 0 | 2 |  |  | 0.03491 | √ | 0.0698 | 0.0698 | C |  |  | Param.Algorithm.Shutdown |  | Observer | Administrator
P_FastShutdownPitchRate | Pitch | Open-loop pitch rate for fast shutdown | float | 0 | 2 |  |  | 0.03491 | √ | 0.10472 | 0.1396 | C |  | FastShutdownPitchRate | Param.Algorithm.Shutdown |  | Observer | Administrator
P_FastShutdownDecreasedPitchRate | Pitch | Open-loop pitch rate for fast shutdown decreased | float | 0 | 2 |  |  | 0.03491 |  | 0.0349 | 0.0349 | C |  | FastShutdownDecreasedPitchRate | Param.Algorithm.Shutdown |  | Observer | Administrator
P_SlowShutdownPitchRate | Pitch | Open-loop pitch rate for a slow open-loop shutdown | float | 0 | 2 |  |  | 0.03491 | √ | 0.05236 | 0.05236 | C |  | SlowShutDownPitchRate | Param.Algorithm.Shutdown |  | Observer | Administrator
P_ShutdownReducedPitchRateFactor | Vspr | Pitch rate reduction factor for phasing out IPC in open loop shutdowns | float | 0 | 2 |  |  | 0.7 | √ | 0.7 | 0.7 | C |  | ShutdownReducedPitchRateFactor | Param.Algorithm.Shutdown |  | Observer | Administrator
P_ShutdownPitchDeadBand | Vspr | Pitch dead band for phasing out IPC in open loop shutdowns | float | 0 | 1 |  |  | 0.0175 | √ | 0.0175 | 0.0175 | C |  | ShutdownPitchDeadBand | Param.Algorithm.Shutdown |  | Observer | Administrator
P_GridLossShutdownPitchRate | Vspr | Open-loop pitch rate for grid-loss shutdown | float | 0 | 2 |  |  | 0.03491 | √ | 0.105 | 0.105 | C |  | GridLossShutdownPitchRate | Param.Algorithm.Shutdown |  | Observer | Administrator
P_GridLossTorqueDuration | Vspr | Maximum time over which reaction torque can be maintained in a grid-loss shutdown | float | 0 | 10 |  |  | 0 | √ | 4 | 4 | C |  | GridLossTorqueDuration | Param.Algorithm.Shutdown |  | Observer | Administrator
P_FastShutdownTorqueRateLimit | Vspr | Maximum torque rate limit when fast shut down | float | 0 | 1E10 |  |  | 500000 |  | 500000 | 500000 | C |  | FastShutdownTorqueRateLimit | Param.Algorithm.Shutdown |  | Observer | Administrator
;
; Alarm Thresholds
P_MaxGeneratorSpeedForSwTrip | Vspr | Software overspeed level | float | 0 | 300 |  |  | 1.4458 | √ | 1.260564 | 1E10 | C |  | MaxGeneratorSpeedForSwTrip | Param.Algorithm.Alarm |  | Observer | Administrator
P_SustainedSwOverspeedMaxDuration | Vspr | Maximum duration for sustained Software overspeed | float | 0 | 100 |  |  | 0.5 | √ | 0.5 | 0.5 | C |  | SustainedSwOverspeedMinDuration | Param.Algorithm.Alarm |  | Observer | Administrator
P_SwOverspeedMaxDuration | Vspr | Maximum duration for Software overspeed | float | 0 | 100 |  |  | 0.5 |  | 0.5 | 0.5 | C |  | SustainedSwOverspeedMinDuration | Param.Algorithm.Alarm |  | Observer | Administrator
P_SustainedSwOverspeedPitchrate | Vspr | P_SustainedSwOverspeedPitchrate | float | 0 | 6 |  |  | 0.1745 |  | 2 | 2 | C
P_PitchSanityDynamicActive | Pitch | P_PitchSanityDynamicActive | bool | false | true |  |  | false |  | false | false | C |  | P_PitchSanityDynamicActive | Param.Algorithm.Alarm |  | Observer | Administrator
P_PitchSanityGeneratorSpeedLevel | Pitch | Minimum generator speed for pitch sanity check | float | 0 | 300 |  |  | 1.204 | √ | 1.1205 | 1E10 | C |  | PitchSanityGeneratorSpeedLevel | Param.Algorithm.Alarm |  | Observer | Administrator
P_PitchSanityPitchRateLimit | Pitch | Pitch sanity check rate limit | float | 0 | 0.1 |  |  | -0.04363 | √ | -0.027925 | 0 | C |  | PitchSanityPitchRateLimit | Param.Algorithm.Alarm |  | Observer | Administrator
P_CollectivePitchMinRate | Pitch | Minimum collective pitch rate | float | -0.2 | 0.1 |  |  | -0.1326 | √ | -1.4 | -1.4 | C | If the P_MinimumPitchRateLimit is less than the software rate limit, then this parameter can be used to guard against collective pitch runaways | CollectivePitchMinRate | Param.Algorithm.Alarm |  | Observer | Administrator
P_CollectivePitchMinAngle | Pitch | Minimum collective pitch angle | float | -0.087 | 0.1 |  |  | -0.0436 | √ | -0.008727 | -0.008727 | C | This value should be slighlty lower than P_MinimumFinePitch as the collective pitch angle shoud never be less than that | CollectivePitchMinAngle | Param.Algorithm.Alarm |  | Observer | Administrator
P_CollectivePitchMinAngleForRated | Pitch | Minimum collective pitch angle while at rated | float | -0.087 | 0.1 |  |  | -1.4 | √ | -1.4 | -1.4 | C | This value should be slighlty lower than the scheduled fine pitch at rated | CollectivePitchMinAngleForRated | Param.Algorithm.Alarm |  | Observer | Administrator
P_PowerForCollectivePitchMinAngle | Pitch | Minimum power for alarm on collective pitch angle while at rated | float | 0 | 1E8 |  |  | 10800000 | √ | 10.8E6 | 1E10 | C |  | PowerForCollectivePitchMinAngle | Param.Algorithm.Alarm |  | Observer | Administrator
P_MinIndivPitchAngle | Pitch | Minimim individual blade Pitch Angle Demand to avoid stall | float | -1 | 1 |  |  | -0.043633 | √ | -0.0349065 | -0.0349065 | C |  | MinimumIndividualPitchAngle | Param.Algorithm.Alarm |  | Observer | Administrator
P_MaxPitchDemandDifference | Pitch | Maximum difference between pitch demands of any two blades | float | 0 | 0.1 |  |  | 1.4 | √ | 1.4 | 1.4 | C |  | MaximumPitchDemandDifference | Param.Algorithm.Alarm |  | Observer | Administrator
P_MaxPitchPositionDifference | Pitch | Maximum difference between real pitch angle of any two blades | float | 0 | 0.1 |  |  | 0.03491 |  | 1.4 | 1.4 | C |  | MaximumPitchDemandDifference | Param.Algorithm.Alarm |  | Observer | Administrator
P_MaximumPitchFollowingError | Pitch | Maximum pitch following error | float | 0 | 2 |  |  | 0.05236 | √ | 0.0611 | 0.0611 | C |  | MaximumPitchFollowingError | Param.Algorithm.Alarm |  | Observer | Administrator
P_MaximumPitchFollowingErrorRate | Pitch | Maximum pitch following error rate | float | 0 | 2 |  |  | 0.0611 | √ | 0.0611 | 0.0611 | C |  | MaximumPitchFollowingErrorRate | Param.Algorithm.Alarm |  | Observer | Administrator
P_PitchFollowingErrorMaxDuration | Pitch | Maximum duration for pitch following error above threshold | float | 0 | 100 |  |  | 1 | √ | 1 | 1 | C |  | PitchFollowingErrorMaxDuration | Param.Algorithm.Alarm | s | Observer | Administrator
P_MaxPitchForFollowingError | Pitch | Maximum pitch to evaluate following error | float | 0 | 2 |  |  | 1.4 | √ | 1.4 | 1.4 | C |  | MaxPitchForFollowingError | Param.Algorithm.Alarm |  | Observer | Administrator
P_MaximumPitchFollowingErrorVspr | Pitch | Maximum estimated pitch following error | float | 0 | 2 |  |  | 0.0349 | √ | 0.02 | 0.0349 | C |  | MaximumPitchFollowingErrorVspr | Param.Algorithm.Alarm |  | Observer | Administrator
P_MaxIpcDemandError | Pitch | Maximum value for IPC demand error | float | 0 | 2 |  |  | 1.4 | √ | 0.02618 | 0.02618 | C |  | MaximumIpcDemandError | Param.Algorithm.Alarm |  | Observer | Administrator
P_LowPitchAngleOverspeedSpeedLevel | Pitch | Minimum generator speed level for low pitch angle overspeed | float | 0 | 1000 |  |  | 1.4118 | √ | 1.185 | 1E10 | C |  | LowPitchAngleOverspeedSpeedLevel | Param.Algorithm.Alarm |  | Observer | Administrator
P_LowPitchAngleOverspeedPitchLevel | Pitch | Minimum pitch limit for low pitch angle overspeed | float | -0.1 | 1.5 |  |  | 0.05236 | √ | 0.052 | 0.0611 | C |  | LowPitchAngleOverspeedPitchLevel | Param.Algorithm.Alarm |  | Observer | Administrator
P_MinWindSpeedForYawError | Yaw | To be refined at commissioning. It is dependent on the anemometry device used and the location of the sensor. | float | 1 | 4 |  |  | 4 | √ | 2 | 2 | C |  | MinWindSpeedForYawError | Param.Algorithm.Alarm |  | Observer | Administrator
P_MinWindSpeedForYawErrorFinePitch | Yaw | To be refined at commissioning. It is dependent on the anemometry device used and the location of the sensor. | float | 1 | 4 |  |  | 7.5 | √ | 2 | 2 | C |  | MinWindSpeedForYawError | Param.Algorithm.Alarm |  | Observer | Administrator
P_HighYawErrorYawAvT | Yaw | Averaging time constant for yaw error signal used in yaw error alarm | float | 0 | 1000 |  |  | 3 | √ | 3 | 3 | C |  | HighYawErrorYawAvT | Param.Algorithm.Alarm |  | Observer | Administrator
P_HighYawErrorWindSpeedAvT | Yaw | Averaging time constant for wind speed signal used in yaw error alarm | float | 0 | 1000 |  |  | 30 | √ | 30 | 30 | C |  | HighYawErrorWindSpeedAvT | Param.Algorithm.Alarm |  | Observer | Administrator
P_CutoutWindSpeed1 | Vspr | 10min averaged cut out wind speed | float | 0 | 300 |  |  | 999 |  | 1.260564 | 1E10 | C |  | MaxGeneratorSpeedForSwTrip | Param.Algorithm.Alarm |  | Observer | Administrator
P_CutoutWindSpeed2 | Vspr | 3s averaged cut out wind speed | float | 0 | 300 |  |  | 999 |  | 1.260564 | 1E10 | C |  | MaxGeneratorSpeedForSwTrip | Param.Algorithm.Alarm |  | Observer | Administrator
P_CutoutWindSpeedAvT1 | Vspr | Averaging time constant for wind speed signal used in Cutout alarm | float | 0 | 1000 |  |  | 600 |  | 30 | 30 | C |  | HighYawErrorWindSpeedAvT | Param.Algorithm.Alarm |  | Observer | Administrator
P_CutoutWindSpeedAvT2 | Vspr | Averaging time constant for wind speed signal used in Cutout alarm | float | 0 | 1000 |  |  | 3 |  | 30 | 30 | C |  | HighYawErrorWindSpeedAvT | Param.Algorithm.Alarm |  | Observer | Administrator
P_NacelleAccelerationLimit | Vspr | Nacelle acceleration level | float | 0 | 2 |  |  | 5 |  | 1.176 | 1.176 | C |  | MaximumNacelleAcceleration | Param.Algorithm.Alarm | m/s^2 | Observer | Administrator
P_NacelleAccelerationAvT | Vspr | Averaging time constant for nacelle acceleration | float | 0 | 0.1 |  |  | 0.1 |  | 0.1 | 0.1 | C |  | NacelleAccelerationFilterTime | Param.Algorithm.Alarm | s | Observer | Administrator
P_FilteredGeneratorAccelerationLimit | Gen | Max Filtered Generator Acceleration | float | 0 | 1000 |  |  | 1e10 |  | 1e10 | 1E10 | C |  | FilteredGeneratorAccelerationLimit | Param.Algorithm.Alarm |  | Observer | Administrator
P_GeneratorAccelerationFilterTime1 | Gen | Generator Acceleration Filter Time Constant 1 | float | 0 | 10 |  |  | 1 |  | 1 | 1 | C |  | GeneratorAccelerationFilterTime1 | Param.Algorithm.Alarm |  | Observer | Administrator
P_GeneratorAccelerationFilterTime2 | Gen | Generator Acceleration Filter Time Constant 2 | float | 0 | 10 |  |  | 0.03 |  | 0.03 | 0.03 | C |  | GeneratorAccelerationFilterTime2 | Param.Algorithm.Alarm |  | Observer | Administrator
;
; Parameter values
P_ChannelsVersionNumber | Vspr | Unique Version Number for the channel definitions | uint | 0 | 4294967296 |  |  | 246871119 | √ | 1942847529 | 385824207 | C |  | ChannelsVersionNumber |  |  | Observer | Administrator
P_ControllerCycleTime | Vspr | Period of controller cycle in seconds. Changes only take effect on restarts. | float | 0 | 1 |  |  | 0.02 | √ | 0.02 | 0 | C |  | ControllerCycleTime | Param.Algorithm.Param |  | Observer | Administrator
P_GearboxRatio | Vspr | Gearbox ratio | float | 0 | 200 |  |  | 1 | √ | 1 | 1 | C |  | GearboxRatio | Param.Algorithm.Param |  | Observer | Administrator
P_RotorRadius | Vspr | Rotor radius | float | 0 | 200 |  |  | 69.754 | √ | 160 | 1 | C |  | RotorRadius | Param.Algorithm.Param |  | Observer | Administrator
;
; Configuration for Tests and Simulations
P_DisableCalibrations | Test | Set to prevent in/out calibrations. 0: all enabled, 1: all disabled, higher values: bitmask to enable only specified categories | int | 0 | 1073741824 |  |  | 0 | √ | 0 | 0 | C |  | DisableCalibrations |  |  | Observer | Administrator
;
; State Machine Configuration
P_TraceCategory | Test | 32-bit bitmask determining which trace information messages from core controller to output | uint | 0 | 4294967295 |  |  | 1 | √ | 1 | 1 | C |  | TraceCategory | Param.Algorithm.StateMachine |  | Observer | Administrator
P_NormalShutdownLullDuration | Vspr | Delay in seconds after generator disconnection before ramping pitch | float | 0 | 60 |  |  | 5 | √ | 5 | 5 | C |  | NormalShutdownLullDuration | Param.Algorithm.StateMachine |  | Observer | Administrator
P_PowerRampingLullDuration | Vspr | Delay in seconds after power ramping before switching to the power production state | float | 0 | 60 |  |  | 5 | √ | 5 | 5 | C |  | PowerRampingLullDuration | Param.Algorithm.StateMachine |  | Observer | Administrator
P_ConnectionLullDuration | Vspr | Delay in seconds after PCS connection before activating torque control | float | 0 | 60 |  |  | 5 | √ | 5 | 5 | C |  | ConnectionLullDuration | Param.Algorithm.StateMachine |  | Observer | Administrator
P_LvrtLullDuration | Vspr | Delay in seconds after a pitch kick before re-activating alarms to avoid spurious trips | float | 0 | 5 |  |  | 1 | √ | 1 | 1 | C | Set an appropriate time for the system to settle before switching to power ramping | LvrtLullDuration | Param.Algorithm.StateMachine |  | Observer | Administrator
;
; Generator configuration
P_MaximumGeneratorTorque | Vspr | Maximum torque limit. | float | 0 | 100000 |  |  | 2457400 | √ | 60000000 | 15000 | C |  | MaximumGeneratorTorque | Param.Algorithm.Generator |  | Observer | Administrator
;
; Pitch System
P_PitchActuatorType | Vspr | 0 = Pitch position 1 = Pitch rate | int | 0 | 1 |  |  | 1 | √ | 1 | 0 | C |  | PitchActuatorType | Param.Algorithm.Pitch |  | Observer | Administrator
P_PitchAngleTolerance | Vspr | The tolerance for testing pitch limits | float | 0 | 2 |  |  | 0.034 | √ | 0.034 | 0.034 | C |  | PitchAngleTolerance | Param.Algorithm.Pitch |  | Observer | Administrator
P_PitchActuatorDelay | Vspr | Estimated delay in actuator response to pitch demand | float | 0 | 2 |  |  | 0.06 | √ | 0.06 | 0 | C | Used for pitch following trips. Should match DSICON mapping. | PitchActuatorDelay | Param.Algorithm.Pitch |  | Observer | Administrator
;
; Speed control
P_SyncSpeedTol | Vspr | Tolerance for generator speed control during synchronisation | float | 0 | 100 |  |  | 0.05 | √ | 5 | 5 | C |  | SyncSpeedTol | Param.Algorithm.SpeedControl |  | Observer | Administrator
P_GenSpeedAtSyncSpeedRequiredTime | Vspr | Required time within the speed sync tolerance before engaging the contactor | float | 0 | 60 |  |  | 5 | √ | 5 | 5 | C |  | GenSpeedAtSyncSpeedRequiredTime | Param.Algorithm.SpeedControl |  | Observer | Administrator
;
; Pitch rate deadband
P_PitchRateDeadband |  |  | float | 0 | 0.1 |  |  | 0.00349 | 6.9808E-04 | 6.9808E-04 | C |  | PitchRateDeadband | Param.Algorithm.Pitch |  | Observer | Administrator
;
; Algorithm configuration
P_TorqueControlStepMultiplier | Vspr | Torque-speed loop timestep multiplier | int | 1 | 10 |  |  | 1 | √ | 1 | 1 | C |  | TorqueControlStepMultiplier | Param.Algorithm.Config |  | Observer | Administrator
P_PitchControlStepMultiplier | Vspr | Pitch-speed loop timestep multiplier | int | 1 | 10 |  |  | 1 | √ | 1 | 2 | C |  | PitchControlStepMultiplier | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueLoopBlockSize | Vspr | Torque-speed block averaging samples | int | 1 | 10 |  |  | 1 | √ | 1 | 1 | C |  | TorqueLoopBlockSize | Param.Algorithm.Config |  | Observer | Administrator
P_PitchLoopBlockSize | Vspr | Pitch-speed block averaging samples | int | 1 | 10 |  |  | 1 | √ | 1 | 2 | C |  | PitchLoopBlockSize | Param.Algorithm.Config |  | Observer | Administrator
P_OptimalModeGain | Vspr | Optimal mode gain | float | 0 | 100 |  |  | 1.248E+06 | √ | 2.699E+06 | 0 | C |  | OptimalModeGain | Param.Algorithm.Config |  | Observer | Administrator
P_IndividualPitchCorrectionFactor | Vspr | Pitch drift correction factor | float | 0 | 100 |  |  | 0.3 | √ | 1 | 1 | C |  | IndividualPitchCorrectionFactor | Param.Algorithm.Config |  | Observer | Administrator
P_KpStyle | Vspr | Pitch-speed loop Proportional gain schedule interpolation type | int | -5 | 5 |  |  | -1 | √ | -1 | -1 | C |  | KpStyle | Param.Algorithm.Config |  | Observer | Administrator
P_KiStyle | Vspr | Pitch-speed loop Integral gain schedule interpolation type | int | -5 | 5 |  |  | 1 | √ | 1 | 1 | C |  | KiStyle | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedProportionalGain | Vspr | Pitch-speed loop proportional gain (not really used just for powegains) | float | 0 | 10000 |  |  | 1.4 |  | 29305376 | 0 | C |  | TorqueSpeedProportionalGain | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedIntegralGain | Vspr | Pitch-speed loop integral gain(not really used just for powegains) | float | 0 | 10000 |  |  | 0.4 |  | 4571415 | 0 | C |  | TorqueSpeedIntegralGain | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedDerivativeGain | Vspr | Pitch-speed loop derivative gain(not really used just for powegains) | float | 0 | 10000 |  |  | 0 |  | 0 | 0 | C |  | TorqueSpeedDerivativeGain | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedDerivativeTimeConstant | Vspr | Pitch-speed loop derivative term time constant | float | 0 | 10 |  |  | 0.65 | √ | 0 | 0 | C |  | PitchSpeedDerivativeTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedDerivativeTimeConstantSlow | Vspr | Pitch-speed loop derivative term time constant Slow | float | 0 | 10 |  |  | 0.65 | √ | 0 | 0 | C |  | PitchSpeedDerivativeTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBias | Vspr | Pitch-speed loop bias enabled | bool | false | true |  |  | true | √ | true | true | C |  | PitchBias | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBiasPowerFactor | Vspr | Fraction of rated power at which pitch-speed loop bias reaches maximum | float | 0 | 1 |  |  | 0.7 | √ | 0.7 | 0.7 | C |  | PitchBiasPowerFactor | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBiasSpeedFactor | Vspr | Factor applied to pitch-speed setpoint at maximum bias | float | 0 | 1 |  |  | 0.12 | √ | 0.12 | 0.05 | C |  | PitchBiasSpeedFactor | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBiasFilterUpwardTc | Vspr | Pitch-speed loop bias upward time constant | float | 0 | 100 |  |  | 10 | √ | 10 | 10 | C |  | PitchBiasFilterUpwardTc | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBiasFilterDownwardTc | Vspr | Pitch-speed loop bias downward time constant | float | 0 | 100 |  |  | 5 | √ | 5 | 5 | C |  | PitchBiasFilterDownwardTc | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBiasFilterUpwardRateLimit | Vspr | Pitch-speed loop bias upward rate limit | float | 0 | 1000 |  |  | 0 | √ | 0 | 0 | C | 0 means unlimited | PitchBiasFilterUpwardRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_PitchBiasFilterDownwardRateLimit | Vspr | Pitch-speed loop bias downward rate limit | float | 0 | 1000 |  |  | 0 | √ | 0 | 0 | C | 0 means unlimited | PitchBiasFilterDownwardRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_PitchPowerGains | Vspr | Pitch-speed loop bias enabled. Bias and PowerGains should be enable only one of them!!!! This also be set as the flag to identifiy which controller to be used | bool | false | true |  |  | false |  | true | true | C |  | PitchBias | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedPowerPIProportionalGain | Vspr | Pitch-speed loop Power PI proportional gain | float | 0 | 1E10 |  |  | 1e-07 |  | 29305376 | 0 | C |  | TorqueSpeedProportionalGain | Param.Algorithm.Config |  | Observer | Administrator
P_PitchSpeedPowerPIIntegralGain | Vspr | Pitch-speed loop Power PI integral gain | float | 0 | 1E10 |  |  | 1e-08 |  | 4571415 | 0 | C |  | TorqueSpeedIntegralGain | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBias | Vspr | Torque-speed loop bias enabled | bool | false | true |  |  | true | √ | true | true | C |  | TorqueBias | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasPitchMargin | Vspr | Pitch margin above fine at which torque-speed loop bias reaches maximum | float | 0 | 1 |  |  | 0.0873 | √ | 0.0873 | 0.0873 | C |  | TorqueBiasPitchMargin | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasSpeedFactor | Vspr | Factor applied to torque-speed setpoint at maximum bias | float | 0 | 1 |  |  | 0.25 | √ | 0.25 | 0.25 | C |  | TorqueBiasSpeedFactor | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasFilterUpwardTc | Vspr | Torque-speed loop bias upward time constant | float | 0 | 100 |  |  | 30 | √ | 30 | 30 | C |  | TorqueBiasFilterUpwardTc | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasFilterDownwardTc | Vspr | Torque-speed loop bias downward time constant | float | 0 | 100 |  |  | 10 | √ | 10 | 10 | C |  | TorqueBiasFilterDownwardTc | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasFilterUpwardRateLimit | Vspr | Torque-speed loop bias upward rate limit | float | 0 | 100000 |  |  | 0 | √ | 0 | 0 | C | 0 means unlimited | TorqueBiasFilterUpwardRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasFilterDownwardRateLimit | Vspr | Torque-speed loop bias downward rate limit | float | 0 | 100000 |  |  | 0 | √ | 0 | 0 | C | 0 means unlimited | TorqueBiasFilterDownwardRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_FinePitchScheduleAvT | Vspr | Fine pitch schedule averaging time | float | 0 | 60 |  |  | 5 | √ | 1 | 1 | C |  | FinePitchScheduleAvT | Param.Algorithm.Config |  | Observer | Administrator
P_FinePitchScheduleYawAvT | Vspr | P_FinePitchScheduleYawAvT | float | 0 | 60 |  |  | 5 | √ | 1 | 1 | C |  | FinePitchScheduleYawAvT | Param.Algorithm.Config |  | Observer | Administrator
P_StallFinePitchWindSpeedAvT | Vspr | Averaging time constant for wind speed signal used in Stall | float | 0 | 60 |  |  | 2 |  |  | C |  | StallFinePitchWindSpeedAvT | Param.Algorithm.Config |  | Observer | Administrator
P_GentlePitDropMeasuredPitchAvT | Vspr | Averaging time constant for measured pitch average time for Gentle Pitch Drop Control | float | 0 | 300 |  |  | 30 |  | 30 | 30 | C |  | Gentle Pitich Drop Measured Pitch AvT | Param.Algorithm.GentlePitch | s | Observer | Administrator
P_GainScheduleAveragingTimeConstant | Vspr | Pitch-speed loop gain schedule averaging time constant | float | 0 | 60 |  |  | 0 | √ | 0 | 0 | C |  | GainScheduleAveragingTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_PitchAccelerationLimit | Pitch | Collective pitch acceleration limit, absolute value. Zero disables acceleration limit. | float | 0 | 2 |  |  | 0.349 | √ | 0.698 | 0 | C |  | PitchAccelerationLimit | Param.Algorithm.Config |  | Observer | Administrator
P_UltimateRateLimit | Vspr | Ultimate pitch rate limit (including nacelle feedback and IPC) | float | 0 | 2 |  |  | 0.10472 | √ | 0.139626 | 0.144836 | C |  | UltimateRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_MaximumTorqueRate | Vspr | Maximum torque rate | float | 0 | 100000000000 |  |  | 10000000000 | √ | 1E10 | 1E10 | C | Normally Rated torque in 1 sec | MaximumTorqueRate | Param.Algorithm.Config |  | Observer | Administrator
P_MinimumTorqueRate | Vspr | Minimum torque rate | float | -100000000000 | 0 |  |  | -10000000000 | √ | -1E10 | -1E10 | C |  | MinimumTorqueRate | Param.Algorithm.Config |  | Observer | Administrator
P_RateLimitMinMaxTorque | Vspr | Enable rate limit for Min and Max Torque | bool | false | true |  |  | false | √ | false | false | C |  | RateLimitMinMaxTorque | Param.Algorithm.Config |  | Observer | Administrator
P_RateLimitOnlyIfNotSat | Vspr | Enable rate limit when torque PID is not saturated | bool | false | true |  |  | false | √ | false | false | C |  | RateLimitOnlyIfNotSat | Param.Algorithm.Config |  | Observer | Administrator
P_ConstantPowerControlFlag | Vspr | Constant power control flag | int | 0 | 1 |  |  | 1 | √ | 1 | 0 | C |  | ConstantPowerControlFlag | Param.Algorithm.Config |  | Observer | Administrator
P_MinimumTorqueFactor | Vspr | Constant power minimum torque factor | float | 0 | 1 |  |  | 0.95 | √ | 0.95 | 0.95 | C |  | MinimumTorqueFactor | Param.Algorithm.Config |  | Observer | Administrator
P_MaximumTorqueFactor | Vspr | Constant power maximum torque factor | float | 1 | 2 |  |  | 1.06 | √ | 1.06 | 1.06 | C |  | MaximumTorqueFactor | Param.Algorithm.Config |  | Observer | Administrator
P_PitchDeadBand | Vspr | Pitch dead band for torque ratchet | float | 0 | 2 |  |  | 0.00349 | √ | 0.0349 | 2 | C |  | PitchDeadBand | Param.Algorithm.Config |  | Observer | Administrator
P_AboveratedYawErrorLimit | Vspr | P_AboveratedYawErrorLimit | float | 0 | 100 |  |  | 0.698 |  | 0.698 | 0.698 | C |  | P_AboveratedYawErrorLimit
P_TorqueSpeedProportionalGain | Vspr | Torque-speed loop proportional gain | float | 0 | 10000 |  |  | 9893502 | √ | 33104004.7382 | 0 | C |  | TorqueSpeedProportionalGain | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueSpeedIntegralGain | Vspr | Torque-speed loop integral gain | float | 0 | 10000 |  |  | 2679490 | √ | 4823377.6977 | 0 | C |  | TorqueSpeedIntegralGain | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueSpeedDerivativeGain | Vspr | Torque-speed loop derivative gain | float | 0 | 10000 |  |  | 0 | √ | 0 | 0 | C |  | TorqueSpeedDerivativeGain | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueSpeedGainFactorMinSpeed | Vspr | Torque-speed loop gain factor minimum speed | float | 0 | 200 |  |  | 1 | √ | 1 | 1 | C |  | TorqueSpeedGainFactorMinSpeed | Param.Algorithm.Config |  | Observer | Administrator
P_DriveTrainDamperGain | Vspr | Drivetrain damper gain | float | 0 | 10000 |  |  | 0 | √ | 0 | 0 | C |  | DriveTrainDamperGain | Param.Algorithm.Config |  | Observer | Administrator
P_DriveTrainDamperTorqueLimit | Vspr | Drivetrain damper torque demand limit | float | 0 | 10000 |  |  | 0 | √ | 0 | 1E10 | C | Normally 3-5% of rated torque | DriveTrainDamperTorqueLimit | Param.Algorithm.Config |  | Observer | Administrator
P_DynamicFinePitchTimeConstant | Vspr | Time constant for dynamic fine pitch modification | float | 0 | 60 |  |  | 5 | √ | 5 | 5 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_TorqueBiasIgnoresDynamicFinePitch | Vspr | Flag for Torque Bias to ignore Dynamic Fine Pitch | int | 0 | 1 |  |  | 1 | √ | 1 | 1 | C | Only used if T_DynamicFinePitch enabled | TorqueBiasIgnoresDynamicFinePitch | Param.Algorithm.Config |  | Observer | Administrator
; Algorithm optional components | [8 empty] | √
;
; v3.85 Non-standard Lidar Configuration
P_V385ControlFlag | Vspr | Bladed v3.85 version lidar control | bool | false | true |  |  | false | √ | false | false | C |  | ConstantPowerControlFlag | Param.Algorithm.Config |  | Observer | Administrator
P_V46PControlFlag | Vspr | Bladed v4.6+version lidar control | bool | false | true |  |  | false | √ | false | false | C |  | ConstantPowerControlFlag | Param.Algorithm.Config |  | Observer | Administrator
P_FFControlEnable | Vspr | Bladed v3.85 version lidar control | bool | false | true |  |  | false | √ | false | false | C |  | ConstantPowerControlFlag | Param.Algorithm.Config |  | Observer | Administrator
P_NumsOfBeams | Vspr | NumsOfBeams | int | 0 | 100 |  |  | 4 |  | 1 | 1 | C | Only used if T_DynamicFinePitch enabled | TorqueBiasIgnoresDynamicFinePitch | Param.Algorithm.Config |  | Observer | Administrator
P_NumsOfOfFocusPlanes | Vspr | NumsOfFocusPlanes | int | 0 | 100 |  |  | 5 |  | 1 | 1 | C | Only used if T_DynamicFinePitch enabled | TorqueBiasIgnoresDynamicFinePitch | Param.Algorithm.Config |  | Observer | Administrator
P_LidarScanPeriod | Vspr | Time constant for dynamic fine pitch modification | float | 0 | 60 |  |  | 0.25 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_AveTurWs | Vspr | AveWindSpeed | float | 0 | 60 |  |  | 16.5 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_Kmax | Vspr | Kmax | float | 0 | 60 |  |  | 0.03229 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_AdaptiveFilterEnable | Vspr | AdaptiveFilterEnable | bool | false | true |  |  | true |  | false | false | C |  | AdaptiveFilterEnable | Param.Algorithm.Config |  | Observer | Administrator
P_AdaptiveFilterOrder | Vspr | AdaptiveFilterOrder | int | 0 | 100 |  |  | 1 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_DelayFrequency | Vspr | DelayFrequency | float | 0 | 60 |  |  | 0.1 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_FFTau | Vspr | Fftau | float | 0 | 60 |  |  | 0.5 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_xHub | Vspr | xHub | float | 0 | 60 |  |  | 4.948 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_LidarFactorKp | Vspr | Kp Factor for Lidar Control | float | 0.5 | 1.5 |  |  | 0.7 |  | 0.7 | 0.7 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_LidarFactorTi | Vspr | Ti Factor for Lidar Control | float | 0.5 | 5 |  |  | 1.0 |  | 0.7 | 0.7 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_DthetaDvMax | Vspr | DthetaDvMax | float | 0 | 60 |  |  | 0.024433 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_SaveLidarRWSEnable | Vspr | Save Lidar RWS in text file | bool | false | true |  |  | false |  | false | false |  | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_FFTransWindEnable | Vspr | FeedForward for transient wind enable | bool | false | true |  |  | false |  | false | false |  | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_LidarSaveLidarRWSFieldMode | Vspr | 0=remote 1=local | float | 0 | 5 |  |  | 1 |  | 10 | 10 |  |  | LidarV0LErrorTimeThreshold | Param.Algorithm.Config |  | Observer | Administrator
P_GRTPitchKickEnable | Vspr | Enable lidar Gust Up Pitchkick control | bool | false | true |  |  | true |  | false | false | C
P_GRTECDPitchKickEnable | Vspr | Enable lidar Gust Up (ECD) Pitchkick control | bool | false | true |  |  | false |  | true | false | C
P_GustTimePeriod | Vspr | GustTimePeriod | float | 0 | 10 |  |  | 3.0 |  |  |  | C
P_GustMovAveTC | Vspr | MovAve time constant for V0L | float | 0 | 1 |  |  | 0.4 |  |  |  | C
P_GRTPitchKickDuration | Vspr | Gust Up Pitch Kick Time Duration | float | 0 | 5 |  |  | 3.0 |  |  |  | C
P_GRTExtraTimeDuration | Vspr | Gust Up Pitch Kick off for Pitch position limit | float | 0 | 50 |  |  | 15 |  |  | C
P_GRTtoFinePitchRateLimit | Vspr | Rate Limit value After The Position Limitation | float | 0 | 1 |  |  | 0.035 |  | 0.035 | C
P_ShearVPitchKickEnable | Vspr | Enable lidar Gust Up Pitchkick control | bool | false | true |  |  | false |  | false | false | C
P_ShearTimePeriod | Vspr | GustTimePeriod | float | 0 | 10 |  |  | 3.0 |  |  |  | C
P_ShearMovAveTC | Vspr | MovAve time constant for V0L | float | 0 | 1 |  |  | 0.4 |  |  |  | C
P_ShearMaxPitchAngle | Pitch | Maximum operable pitch angle for the Shear V | float | 0 | 2 |  |  | 0.0349 | √ | 0.0349 | 0 | C |  | MinimumFinePitch | Param.Algorithm.PowProd | deg | Observer | Administrator
P_ShearCorrectionFactor | Vspr | Correctionfactor for ShearV | float | 0 | 1 |  |  | 0.85 |  | 3.0 |  | C
P_ShearMinAreaGust | Vspr | ShearGustThreshold | float | 0 | 15 |  |  | 1.7 |  |  |  | C
P_ShearPitchKickDuration | Vspr | Gust Up Pitch Kick Time Duration | float | 0 | 5 |  |  | 3.0 |  |  |  | C
P_ShearExtraTimeDuration | Vspr | ShearV Pitch Kick off for Pitch position limit | float | 0 | 50 |  |  | 10 |  |  |  | C
P_ShearHPitchKickEnable | Vspr | Enable lidar Gust Up Pitchkick control | bool | false | true |  |  | false |  | false | false | C
P_ShearTimePeriodH | Vspr | GustTimePeriod | float | 0 | 10 |  |  | 3.0 |  |  |  | C
P_ShearMovAveTCH | Vspr | MovAve time constant for V0L | float | 0 | 1 |  |  | 0.4 |  |  |  | C
P_ShearMaxPitchAngleH | Vspr | Maximum operable pitch angle for the collective pitch controller | float | 0 | 2 |  |  | 0.0349 | √ | 0 | 0 | C |  | MinimumFinePitch | Param.Algorithm.PowProd | deg | Observer | Administrator
P_ShearMinAreaGustH | Vspr | ShearGustThreshold | float | 0 | 15 |  |  | 1.7 |  |  |  | C
P_ShearPitchKickDurationH | Vspr | Gust Up Pitch Kick Time Duration | float | 0 | 5 |  |  | 3.0 |  |  |  | C
P_ShearHExtraTimeDuration | Vspr | ShearH Pitch Kick off for Pitch position limit | float | 0 | 50 |  |  | 10 |  |  |  | C
P_GRTandShearRateLimit | Vspr | GRT and Shear Extra Rate rate limit | float | 0 | 1 |  |  | 0.0349 | √ | 0 | 0 | C | 0 means unlimited | TorqueBiasFilterDownwardRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_LidarV0LErrorTimeThreshold | Vspr | Lidar wind speed error threshold | float | 0 | 60000 |  |  | 10 |  | 10 | 10 |  |  | LidarV0LErrorTimeThreshold | Param.Algorithm.Config |  | Observer | Administrator
P_GRTDynFinePitchEnable | Vspr | Enable lidar Gust Down Dynamic fine pitch control | bool | false | true |  |  | false |  | false | false | C
P_GustDownThreshold | Vspr | GustDownThreshold | float | -15 | 0 |  |  | -6.0 |  |  |  | C
P_GRTDynFinePitchDuration | Vspr | Gust Down Dynamic Fine Pitch Time Duration | float | 0 | 30 |  |  | 15 |  |  |  | C
;
; Eews
P_EewsEnable | Vspr | EewsCal Flag | bool | false | true |  |  | false | √ | false | false | C |  | ConstantPowerControlFlag | Param.Algorithm.Config |  | Observer | Administrator
P_Airdensity | Vspr | Airdensity | float | 0 | 60 |  |  | 1.225 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_Jrotor | Vspr | Jrotor | float | 0 | 60 |  |  | 96549610 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
P_GeneratorSpeedAvt | Vspr | GeneratorSpeedAvt | float | 0 | 60 |  |  | 0.4 |  | 0.25 | 0.25 | C | Only used if T_DynamicFinePitch enabled | DynamicFinePitchTimeConstant | Param.Algorithm.Config |  | Observer | Administrator
;
; Nacelle Acceleration Feedback
P_NacelleAccFAEnabled | Vspr | Nacelle acceleration feedback enabled | bool | false | true |  |  | false | √ | false | false | C |  | NacelleAccFAEnabled | Param.Algorithm.NAF |  | Observer | Administrator
P_NacelleAccFAGain | Vspr | Nacelle acceleration feedback gain | float | 0 | 10000 |  |  | 0.03 | √ | 0.0035 | 0 | C |  | NacelleAccFAGain | Param.Algorithm.NAF |  | Observer | Administrator
P_NacelleAccFABelowRated | Vspr | Nacelle acceleration feedback active below rated | bool | false | true |  |  | false | √ | false | false | C |  | NacelleAccFABelowRated | Param.Algorithm.NAF |  | Observer | Administrator
P_NacelleAccFAIntegralTC | Vspr | Nacelle acceleration feedback time constant (instead of integral gain) | float | 0 | 100 |  |  | 0 | √ | 0 | 0 | C |  | NacelleAccFAIntegralTC | Param.Algorithm.NAF |  | Observer | Administrator
P_NacelleAccFASchedPowerAveragingTime | Vspr | Nacelle acceleration feedback gain schedule averaging time | float | 0 | 60 |  |  | 0 | √ | 0 | 0 | C |  | NacelleAccFASchedPowerAveragingTime | Param.Algorithm.NAF |  | Observer | Administrator
P_NacelleAccMaxYawError | Vspr | Exit Nacelle mode when Yaw Error exceed this value | float | 0 | 3.14 |  |  | 1.0472 |  | 1.0472 | 1.0472 | C |  | NacelleAccFASchedPowerAveragingTime | Param.Algorithm.NAF |  | Observer | Administrator
;
;Non linear parameters Dual PS_PI schedule
P_DualPitchSpeedGainsEnable | Vspr | Pitch-speed loop Dual PID gains | bool | false | true |  |  | true | √ | true | false | C |  | DualPitchSpeedGainsEnable | Param.Algorithm.Config |  | Observer | Administrator
P_DualPitchSpeedGainsSpeedThreshold | Vspr | Filtered generator speed value above which dual Pitch-Speed Gains used | float | 0 | 2 |  |  | 1.2851 | √ | 1.1781 | 0 | C |  | DualPitchSpeedGainsSpeedThreshold | Param.Algorithm.Config |  | Observer | Administrator
P_DualPitchSpeedGainsSpeedDuration | Vspr | Minimum duration of higher gain used after threshold crossing | float | 0 | 10 |  |  | 1 | √ | 3 | 0 | 0 |  | DualPitchSpeedGainsSpeedDuration | Param.Algorithm.Config |  | Observer | Administrator
;
;Non linear parameters
P_ExtraPitchRateAboveThreshold | Vspr | First Pitch kick amplitude (EOG detector A) after NL2 above threshold | float | 0 | 1 |  |  | 0 |  | 0.035 | 0.035 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_DisableNonLinearTermBelowQdemValue | Vspr | To disable pitch kicks below rated | float | 0 | 1E5 |  |  | 1804820 | √ | 4500000 | 5000000 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearAcrDyWaitTime | Vspr | Once triggerd, disable for some time | float | 0 | 600 |  |  | 20 | √ | 30 | 30 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_QdemMovAvTC | Vspr | Filtering time constant demanded torque | float | 0 | 100 |  |  | 5 | √ | 5 | 5 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_EEdotThresholdAsymMovAvDownTc | Vspr | To prevent Eedot threshold dropping too quickly with pitch | float | 0 | 100 |  |  | 3 | √ | 3 | 3 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_ExtraPitchRateAboveThresholdEEdot | Vspr | Second Pitch kick amplitude (ECD+WDC) | float | 0 | 0.1 |  |  | 0 | √ | 0.07854 | 0.035 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_LowestTorsionalModeHalfPeriod | Vspr | Half period in seconds of lowest torsional mode | float | 0 | 1 |  |  | 0.36 | √ | 0.36 | 0.36 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearAcrDyTimeLimit | Vspr | P_NonLinearAcrDyTimeLimit | float | 0 | 50 |  |  | 1.5 | √ | 1.5 | 1.5 |  |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_ExtraPitchRateGenAcc | Vspr | Third Pitch kick amplitude (EOG detector B) | float | 0 | 3 |  |  | 0.09 | √ | 0.09 | 0 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearDelayAfterTrip | Vspr | Delay after NL2 triped compare generator acceleration against threshold | float | 0 | 3 |  |  | 1.2 | √ | 0.1 | 0 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_MinKickDurationEOGB | Vspr | Minimum pitch kick duration for EOG detector B | float | 0 | 2 |  |  | 1 | √ | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearNormalStopExtraPRate | Vspr | (Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint)=Prate(deg/s) | float | 0 | 20 |  |  | 0 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearNormalStopMinPitchAngle | Vspr | Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint | float | 0 | 20 |  |  | 8 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearNormalStopExtraPRateDuration | Vspr | Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint | float | 0 | 20 |  |  | 0.3 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearNormalStopNaccAccFA | Vspr | Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint | float | 0 | 20 |  |  | 0.5 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearNormalStopNaccAccFADuration | Vspr | (Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint)=Prate | float | 0 | 20 |  |  | 0.7 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearExtraGenAccMaxPitchAngle | Vspr | (Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint)=Prate | float | 0 | 20 |  |  | 3 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_NonLinearExtraGenAccThreshold | Vspr | (Pitch angle >setPoint&& NaccAccFA>setPoint&&Duration>setPoint)=Prate | float | 0 | 20 |  |  | 0.04 |  | 1 | 1 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickEnable | Vspr | Yaw pitch kick enable flag | bool | false | true |  |  | false |  | true | true | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickYawErrorThreshold | Vspr | Yaw error threshold for yaw pitch kick (rad) | float | 0 | 1.5708 |  |  | 0.5236 |  | 0.5236 | 0.5236 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawErrorMovAvTC | Vspr | Yaw error averaging time | float | 0 | 60 |  |  | 0.2 |  | 0.2 | 0.2 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickWindSpeedMovAvTCLong | Vspr | Wind speed averaging time for gust wind judgment | float | 0 | 60 |  |  | 10 |  | 10 | 10 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickWindSpeedMovAvTCShort | Vspr | Wind speed averaging time for gust wind judgment | float | 0 | 60 |  |  | 0.1 |  | 10 | 10 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickGustWindThreshold | Vspr | Gust wind threshold for yaw pitch kick | float | 0 | 30 |  |  | 4.5 |  | 4.5 | 4.5 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickPowerThreshold | Vspr | Minimum power threshold for yaw pitch kick | float | 0 | 1E10 |  |  | 1600000 |  | 1600000 | 1600000 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
P_YawPitchKickPowerAccThreshold | Vspr | Minimum power accleraction threshold for yaw pitch kick | float | 0 | 1E6 |  |  | 200000 |  | 200000 | 200000 | C |  |  | Param.Algorithm.Config |  | Observer | Administrator
;
;HighTurbulenceDerating
P_NacAccXPitchScheduleEnable | Vspr | Fine pitch schedule flag based on nacelle acceleration for-aft value | bool | false | true |  |  | false |  | true | true | C
P_NacAccXPitchScheduleAvT | Vspr | Nacelle accleration for-aft value averaging time | float | 0 | 600 |  |  | 30 |  | 1 | 1 | C |  | NacAccXPitchScheduleAvT | Param.Algorithm.Config |  | Observer | Administrator
P_NacAccXBelowThresholdMinDuration | Vspr | Nacelle accleration for-aft threshold | float | 0 | 600 |  |  | 60 |  | 1 | 1 | C |  | NacAccXBelowThresholdbeMaxDuration | Param.Algorithm.Config |  | Observer | Administrator
P_NacAccXAboveThresholdMinDuration | Vspr | P_NacAccXAboveThresholdMinDuration | float | 0 | 600 |  |  | 3 |  | 1 | 1 | C |  | NacAccXBelowThresholdbeMaxDuration | Param.Algorithm.Config |  | Observer | Administrator
P_MinimumFinePitchBasedonNacAccX | Vspr | Minimum pitch angle when nacelle accleration for-aft above threshold | float | 0 | 0.5236 |  |  | 0.08727 |  | 0.08727 | 0.08727 | C |  | MinimumFinePitchBasedonNacAccX | Param.Algorithm.Config |  | Observer | Administrator
P_NacAccXPitchScheduleRateLimit | Vspr | Pitch rate up limit during fine pitch schedule based on nacelle acceration for-aft be trigged | float | 0 | 0.08727 |  |  | 0.008727 |  | 0.008727 | 0.008727 | C |  | NacAccXPitchScheduleUpRateLimit | Param.Algorithm.Config |  | Observer | Administrator
P_MinWindSpeedForNacAccXPitchSched | Vspr | To be refined at commissioning. It is dependent on the anemometry device used and the location of the sensor. | float | 1 | 25 |  |  | 3 |  | 2 | 2 | C |  | MinWindSpeedForYawError | Param.Algorithm.Alarm |  | Observer | Administrator
; IPC
P_IpcStrategySelect | Vspr | 1P IPC strategy select: 0 No IPC，1 old 1P IPC， 2 new 1P IPC | float | 0 | 10 |  |  | 0 | √ |  |  | C |  | P_IpcStrategySelect | Param.Algorithm.IPC |  | Observer | Administrator
;Old
P_IpcMaximumPitchComponent | Vspr | Maximum pitch component added by IPC | float | 0 | 2 |  |  | 0 | √ | 0 | 0.03491 | C | use 5 deg (0.0873), still hitting rate limit but lower load | IpcMaximumPitchComponent | Param.Algorithm.IPC |  | Observer | Administrator
P_IPCBladeBendingMomentLimitEnable | Vspr | IPC blade bending moment limit enabled | bool | false | true |  |  | false | √ | false | false | C |  | IPCMinimumBladeBendingMoment | Param.Algorithm.IPC |  | Observer | Administrator
P_IPCBladeBendingMomentLimitTime | Vspr | Once triggerd, Sustain for some time | float | 0 | 1000 |  |  | 20 | √ | 20 | 20 | C |  | IPCMinimumBladeBendingMoment | Param.Algorithm.IPC |  | Observer | Administrator
P_IPCMinimumBladeBendingMoment | Vspr | Minimum blade bending moment to start IPC | float | 0 | 100000000 |  |  | 23000000 | √ | 0 | 0 | C |  | IPCMinimumBladeBendingMoment | Param.Algorithm.IPC |  | Observer | Administrator
P_IPCAboveThresholdMinDuration | Vspr | P_IPCMinimumBladeBendingMomentAvt | float | 0 | 60 |  |  | 1e-05 |  | 0 | 0 | C
P_IPCMinimumBladeBendingMomentMovAvTC | Vspr | Filtering time constant for blade bending moment | float | 0 | 30 |  |  | 1 | √ | 0 | 0 | C |  | IPCMinimumBladeBendingMomentMovAvTC | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcProportionalGain | Vspr | IPC Proportional Gain | float | 0 | 1000000 |  |  | 0 | √ | 0 | 0 | C |  | IpcProportionalGain | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcIntegralGain | Vspr | IPC Integral Gain | float | 0 | 1000000 |  |  | 7.14e-09 | √ | 7.14E-9 | 0 | C |  | IpcIntegralGain | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcTimeShift | Vspr | IPC Time Shift | float | 0 | 10 |  |  | 0 |  | 0 | 0 | C |  | IpcTimeShift | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcPhaseShift | Vspr | IPC Azimuthal phase shift | float | -6.2832 | 6.2832 |  |  | 0.6981 | √ | 0.47538 | 0 | C |  | IpcPhaseShift | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcMinimumPitch | Vspr | IPC Minimum Pitch | float | 0 | 0 |  |  | -0.01745 | √ | -0.00872664 | 0 | C |  | IpcMinimumPitch | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcMaximumPitch | Vspr | IPC MaximumPitch | float | 0 | 2 |  |  | 1.57 | √ | 1.57 | 1.57 | C |  | IpcMaximumPitch | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcPitchLimitsEnabled | Vspr | IPC Pitch Limits Enabled Flag | bool | false | true |  |  | true |  | true | false | C |  | IpcPitchLimitsEnabled | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcDqPitchRateLimit | Vspr | IPC DQ Pitch Absolute Rate Limit | float | 0 | 1000000 |  |  | 1000 |  | 1000 | 1000 | C |  | IpcDqPitchRateLimit | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcMyHighPassEnable | Vspr | IPC My high pass filter enable | bool | false | true |  |  | false |  | false | false | C |  | IpcMyHighPassEnable | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcMyHighPassTimeConstant | Vspr | IPC My high pass filter time constant | float | 0 | 1000 |  |  | 60 |  | 60 | 60 | C |  | IpcMyHighPassTimeConstant | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcBladePosition1 | Vspr | Position number of Blade 1 | int | 1 | 3 |  |  | 1 |  | 1 | 1 | C |  | IpcBladePosition1 | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcBladePosition2 | Vspr | Position number of Blade 2 | int | 1 | 3 |  |  | 2 |  | 2 | 2 | C |  | IpcBladePosition2 | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcBladePosition3 | Vspr | Position number of Blade 3 | int | 1 | 3 |  |  | 3 |  | 3 | 3 | C |  | IpcBladePosition3 | Param.Algorithm.IPC |  | Observer | Administrator
;
;New
P_IpcProportionalGain1 | Vspr | IPC Proportional Gain | float | 0 | 1000000 |  |  | 1.0513e-08 |  |  |  | C |  | IpcProportionalGain | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcIntegralGain1 | Vspr | IPC Integral Gain | float | 0 | 1000000 |  |  | 2.1025e-09 |  |  |  | C |  | IpcIntegralGain | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcActivationThreshold | Vspr | Ipc Activation Threshold | float | 0 | 10000000 |  |  | 0 |  | 1500000 | 0.5 | C |  | IpcActivationThreshold | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcAmplitudeLimit | Vspr | Ipc Amplitude Limit | float | 0 | 1000 |  |  | 0.03491 |  | 0.05236 | 10 | C |  | IpcAmplitudeLimit | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcTintRealese | Vspr | Integrator Realse Time | float | 0 | 1000 |  |  | 0.5 |  | 0.5 | 0.5 | C |  | IpcTintRealese | Param.Algorithm.IPC |  | Observer | Administrator
P_IpcPhaseOff1p | Vspr | PhaseOff1p | float | 0 | 1000 |  |  | 0.618 |  |  |  | C |  | PhaseOff1p | Param.Algorithm.IPC |  | Observer | Administrator
;
; 2P IPC
P_2PIpcStrategySelect | Vspr | 2P IPC strategy select: 0 No IPC，1 old 2P IPC， 2 new 2P IPC | float | 0 | 10 |  |  | 0 | √ |  |  | C |  | 2PIpcStrategySelect | Param.Algorithm.2PIPC |  | Observer | Administrator
;Old
P_2PIpcMaximumPitchComponent | Vspr | Maximum pitch component added by 2P IPC | float | 0 | 2 |  |  | 0 | √ | 0.0611 | 0.0611 | C | use 3.5 deg | 2PIpcMaximumPitchComponent | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcMaxAbsPitchRateFilterDownwardTc | Vspr | Filtering time constant Asym filter | float | 0 | 10 |  |  | 3 |  | 3 | 3 | C |  | 2PIpcMaxAbsPitchRateFilterDownwardTc | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcPhaseOutRate | Vspr | Phase out rate of D-Q pitch demands overall rates too high | float | 0 | 1 |  |  | 0.00523 |  | 0.00523 | 0.005 | C |  | 2PIpcPhaseOutRate
P_2PIpcProportionalGain | Vspr | 2P IPC Proportional Gain | float | 0 | 1000000 |  |  | 0 |  | 0 | 0 | C |  | 2PIpcProportionalGain | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcIntegralGain | Vspr | 2P IPC Integral Gain | float | 0 | 1000000 |  |  | 7.41e-09 |  | 7.41E-9 | 0 | C |  | 2PIpcIntegralGain | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcTimeShift | Vspr | 2P IPC Time Shift | float | 0 | 10 |  |  | 0 |  | 0 | 0 | C |  | 2PIpcTimeShift | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcPhaseShift | Vspr | 2P IPC Azimuthal phase shift | float | -6.2832 | 6.2832 |  |  | 1.5708 |  | 0.7 | 0 | C |  | 2PIpcPhaseShift | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcDqPitchRateLimit | Vspr | 2P IPC DQ Pitch Rate Limit - Absolute rate limit value | float | 0 | 1000000 |  |  | 1000 |  | 1000 | 1000 | C |  | 2PIpcDqPitchRateLimit | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcMyHighPassEnable | Vspr | 2P IPC My high pass filter enable | bool | false | true |  |  | false |  | false | false | C |  | 2PIpcMyHighPassEnable | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcMyHighPassTimeConstant | Vspr | 2P IPC My high pass filter time constant | float | 0 | 1000 |  |  | 60 |  | 60 | 60 | C |  | 2PIpcMyHighPassTimeConstant | Param.Algorithm.2PIPC |  | Observer | Administrator
;New
P_2PIpcProportionalGain1 | Vspr | 2P IPC Proportional Gain 1 | float | 0 | 1000000 |  |  | 1.0513e-08 |  |  |  | C |  | 2PIpcProportionalGain | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcIntegralGain1 | Vspr | 2P IPC Integral Gain 1 | float | 0 | 1000000 |  |  | 2.1025e-09 |  |  |  | C |  | 2PIpcIntegralGain | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcActivationThreshold | Vspr | Ipc Activation Threshold | float | 0 | 10000000 |  |  | 0 |  | 6000000 | 0.5 | C |  | 2IpcActivationThreshold | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcAmplitudeLimit | Vspr | Ipc Amplitude Limit | float | 0 | 1000 |  |  | 0.05236 |  | 0.05236 | 10 | C |  | 2PIpcAmplitudeLimit | Param.Algorithm.2PIPC |  | Observer | Administrator
P_2PIpcTintRealese | Vspr | Integrator Realse Time | float | 0 | 1000 |  |  | 0.5 |  | 0.5 | 0.5 | C |  | 2PIpcTintRealese | Param.Algorithm.2PIPC |  | Observer | Administrator
P_IpcPhaseComp2p | Vspr | PhaseComp2p | float | 0 | 1000 |  |  | 0.4849 |  |  |  | C |  | PhaseComp2p | Param.Algorithm.2PIPC |  | Observer | Administrator
;
; IPC Limits
P_IpcMaximumPitchTorqueScheduleAvT | Vspr | IPC Schedule vs Torque Averaging Time | float | 0 | 60 |  |  | 5 | √ | 5 | 5 | C |  | IpcMaximumPitchTorqueScheduleAvT | Param.Algorithm.IPCLimits |  | Observer | Administrator
P_IpcMaximumPitchComponentGenAccAvT | Vspr | IPC Schedule vs Generator Acceleration Averaging Time | float | 0 | 60 |  |  | 3 | √ | 3 | 3 | C |  | IpcMaximumPitchComponentGenAccAvT | Param.Algorithm.IPCLimits |  | Observer | Administrator
P_IpcMinimumPitchPitchScheduleAvT | Vspr | IPC Schedule vs Pitch Averaging Time (minimum pitch) | float | 0 | 60 |  |  | 3 | √ | 3 | 0 | C |  | IpcMinimumPitchPitchScheduleAvT | Param.Algorithm.IPCLimits |  | Observer | Administrator
P_IpcMaximumPitchPitchScheduleAvT | Vspr | IPC Schedule vs Pitch Averaging Time (maximum pitch) | float | 0 | 60 |  |  | 3 | √ | 3 | 3 | C |  | IpcMaximumPitchPitchScheduleAvT | Param.Algorithm.IPCLimits |  | Observer | Administrator
P_IpcMaximumPitchPitchRateScheduleAvT | Vspr | IPC Sched with Pitch AvTime | float | 0 | 60 |  |  | 0.5 | √ | 0.5 | 0.5 | C |  | IpcMaximumPitchPitchRateScheduleAvT | Param.Algorithm.IPCLimits |  | Observer | Administrator
;
; Tower Excusion Zone
P_TowerExcEnabled | Vspr | Tower exclusion zone enabled | bool | false | true |  |  | false | √ | true | false | C |  | TowerExcEnabled | Param.Algorithm.TEZ |  | Observer | Administrator
P_TowerExcLowSpeed | Vspr | Tower exclusion zone low speed | float | 0 | 10000 |  |  | 0.5655 | √ | 0.576 | 0 | C |  | TowerExcLowSpeed | Param.Algorithm.TEZ |  | Observer | Administrator
P_TowerExcHighSpeed | Vspr | Tower exclusion zone high speed | float | 0 | 10000 |  |  | 0.6912 | √ | 0.89011 | 0 | C |  | TowerExcHighSpeed | Param.Algorithm.TEZ |  | Observer | Administrator
P_TowerExcLowSpeedMaxTorque | Vspr | Tower exclusion zone torque limit for upward transition | float | 0 | 10000000000 |  |  | 1770000 | √ | 1.804E6 | 0 | C |  | TowerExcLowSpeedMaxTorque | Param.Algorithm.TEZ |  | Observer | Administrator
P_TowerExcHighSpeedMinTorque | Vspr | Tower exclusion zone torque limit for downward transition | float | 0 | 10000000000 |  |  | 792000 | √ | 1.171E6 | 0 | C |  | TowerExcHighSpeedMinTorque | Param.Algorithm.TEZ |  | Observer | Administrator
P_TowerExcSpeedRate | Vspr | Tower exclusion zone transition generator speed rate | float | 0 | 100 |  |  | 0.0105 | √ | 0.0105 | 0 | C |  | TowerExcSpeedRate | Param.Algorithm.TEZ |  | Observer | Administrator
P_TowerExcWaitTime | Vspr | Tower exclusion zone wait time before transition | float | 0 | 10000000000 |  |  | 60 | √ | 60 | 20 | C |  | TowerExcWaitTime | Param.Algorithm.TEZ |  | Observer | Administrator
;
; System Identification Input Perturbation
P_EnableSysIdDemandPerturbations | Vspr | Optionally activates the demand perturbations | bool | false | true |  |  | false | √ | false | false | C |  | EnableSysIdDemandPerturbations | Param.Algorithm.SystemID |  | Observer | Administrator
P_SpeedSetpointScalePerturbation | Vspr | Speed setpoint scale perturbation factor | float | 0 | 100 |  |  | 1 | √ | 1 | 1 | C |  | SpeedSetpointScalePerturbation | Param.Algorithm.SystemID |  | Observer | Administrator
P_SpeedSetpointOffsetPerturbation | Vspr | Speed setpoint offset perturbation | float | 0 | 200 |  |  | 0 | √ | 0 | 0 | C |  | SpeedSetpointOffsetPerturbation | Param.Algorithm.SystemID |  | Observer | Administrator
P_PerturbationDataFromFile | Vspr | Read perturbation data from file (0 = no, 1 = pitch, 2 = torque) | int | 0 | 2 |  |  | 0 | √ | 0 | 0 | C |  | PerturbationDataFromFile | Param.Algorithm.SystemID |  | Observer | Administrator
P_PitchDemandOffsetPerturbation | Vspr | Pitch demand offset perturbation | float | 0 | 2 |  |  | 0 | √ | 0 | 0 | C |  | PitchDemandOffsetPerturbation | Param.Algorithm.SystemID |  | Observer | Administrator
P_TorqueDemandOffsetPerturbation | Vspr | Torque demand offset perturbation | float | 0 | 1000 |  |  | 0 | √ | 0 | 0 | C |  | TorqueDemandOffsetPerturbation | Param.Algorithm.SystemID |  | Observer | Administrator
P_CyclicPitchId | Vspr | Cyclic pitch test (value denotes IPC order). Overrides IPC. | int | 1 | 5 |  |  | 0 | √ | 0 | 0 | C |  | CyclicPitchId | Param.Algorithm.SystemID |  | Observer | Administrator
P_CyclicPitchAmp | Vspr | Cyclic pitch test amplitude if P_CyclicPitchId > 0 [rad] | float | 2 | 0.17453 |  |  | 0 | √ | 0 | 0.01745 | C |  | CyclicPitchAmp | Param.Algorithm.SystemID |  | Observer | Administrator
P_CyclicPitchPhase | Vspr | Cyclic pitch test phase if P_CyclicPitchId > 0 [rad] | float | 3 | 6.2832 |  |  | 0 | √ | 0 | 0 | C |  | CyclicPitchPhase | Param.Algorithm.SystemID |  | Observer | Administrator
;
; LVRT
P_LvrtPitchDuration | Vspr | Duration of pitch kick during LVRT | float | 0 | 10 |  |  | 0.25 | √ | 0.25 | 0.25 | C | Extend this for more agressive pitch action to avoid overspeed | LvrtPitchDuration | Param.Algorithm.LVRT | s | Observer | Administrator
P_LvrtTorqueLimitRate | Vspr | Torque limit rate of change during LVRT | float | 0 | 1 |  |  | 3500 | √ | 3500 | 3500 | C | This is tunable based on how quick you want the torque to ramp after a LVE | LvrtTorqueLimitRate | Param.Algorithm.LVRT |  | Observer | Administrator
;
; Timing performance alarm thresholds
P_ExecutionTimeOverrunThreshold | Vspr | Maximum allowed controller execution time before shutdown | float | 0.02 | 1 |  |  | 0.015 | √ |  |  | C |  | Execution Time Overrun Threshold | Param.Algorithm.Perf | s | Observer | Administrator
P_ShortAvgCycleTimeMismatchFactor | Vspr | Percent tolerance threshold for short averaged cycle time mismatch alarm | float | 0.01 | 1 |  |  | 0.1 | √ |  |  | C |  | Short Avg Cycle Time Mismatch Factor | Param.Algorithm.Perf | s | Observer | Administrator
P_LongAvgCycleTimeMismatchFactor | Vspr | Percent tolerance threshold for long averaged cycle time mismatch alarm | float | 0.01 | 1 |  |  | 0.05 | √ |  |  | C |  | Long Avg Cycle Time Mismatch Factor | Param.Algorithm.Perf | s | Observer | Administrator
;
;DynamicPowerControl
P_PowerShootEnabled | Vspr | Power Shoot control enabled | bool | false | true |  |  | false |  | true | C |  | Power Shoot Enabled | Param.Algorithm.PowerShoot |  | Observer | Administrator
P_PowerShootPowerIncreasedFactor | Vspr | Power shoot increased power factor | float | 0 | 2 |  |  | 1.03 |  | 1 | C |  | Power shoot increased power factor | Param.Algorithm.PowerShoot |  | Observer | Administrator
P_PowerShootTriggerDuration | Vspr | Duration of power shoot cross rated power | float | 0 | 100 |  |  | 30 |  | 3 | C |  | Duration of power shoot cross rated power | Param.Algorithm.PowerShoot |  | Observer | Administrator
P_PowerShootQdemMovAvTC | Vspr | Filtering time constant demanded torque | float | 0 | 100 |  |  | 0.2 |  | 5 | C |  | Filtering time constant demanded torque | Param.Algorithm.PowerShoot |  | Observer | Administrator
P_PowerShootQdemFactor1 | Vspr | P_PowerShootQdemFactor1 | float | 0 | 1 |  |  | 0.95 |  | 0.95 | C |  | Filtering time constant demanded torque | Param.Algorithm.PowerShoot |  | Observer | Administrator
P_PowerShootQdemFactor2 | Vspr | P_PowerShootQdemFactor2 | float | 0 | 1 |  |  | 0.90 |  | 0.95 | C |  | Filtering time constant demanded torque | Param.Algorithm.PowerShoot |  | Observer | Administrator
;
;额定转速在过渡段提升
P_AveragePitchAvT | Vspr | 风机运行III区域额定转速提升查表的桨角平均时间 | float | 0 | 100 |  |  | 10 |  |  |  | C |  |  | Param.Algorithm.Startup | s | Observer | Administrator
P_SpeedUpgradeRateLimit | Vspr |  | float | 0 | 1 |  |  | 0.001 |  |  |  | C |  |  | Param.Algorithm.Startup |  | Observer | Administrator
;部分风速段额定功率提升
P_AverageWindSpeedAvT | Vspr |  | float | 0 | 100 |  |  | 30 |  |  |  | C |  |  | Param.Algorithm.Startup | s | Observer | Administrator
P_PowerIncreaseFactorRateLimit | Vspr |  | float | 0 | 1 |  |  | 0.01 |  |  |  | C |  |  | Param.Algorithm.Startup |  | Observer | Administrator
;GeneratorSpeedDynamicControl
P_HighGenSpeedDynCtrlBiasEnable | Vspr | High generator speed dynamic bias control enabled | bool | false | true |  |  | true |  | true | true | C |  | High generator speed dynamic control enabled | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_HighGenSpeedDynCtrlBiasSpeedThreshold | Vspr | Filtered generator speed value above which High generator speed dynamic control bias used | float | 0 | 2 |  |  | 1.3593 |  | 1.10 | 1.10 | C |  | HighGenSpeedDynCtrlBiasSpeedThreshold | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_HighGenSpeedDynCtrlBiasFactorLimit | Vspr | High generator speed dynamic control bias limit | float | 0 | 0.1 |  |  | 0.05 |  | 0.05 | 0.05 | C |  | High generator speed dynamic control bias limit | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_HighGenSpeedDynCtrlBiasDuration | Vspr | Duration of high generator speed dynamic bias control | float | 0 | 100 |  |  | 5 |  | 5 | 5 | C |  | Duration of high generator speed dynamic bias control | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_HighGenSpeedDynCtrlBiasWaitTime | Vspr | Once triggerd, disable for some time | float | 0 | 600 |  |  | 30 |  | 30 | 30 | C |  | Wait time of high generator speed dynamic bias control next time | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_HighGenSpeedDynCtrlBiasRateLimit | Vspr | HighGenSpeedDynCtrlBiasRateLimit | float | 0 | 1 |  |  | 0.03 |  | 0.015 | 0.015 | C |  | HighGenSpeedDynCtrlBiasRateLimit | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_EstimatedGenAccAvt | Vspr | P_EstimatedGenAccAvt | float | 0 | 10 |  |  | 0.5 |  | 1 | 1 | C |  | P_EstimatedGenAccAvt | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
; Blade clearance
P_ClearanceCtrEnable | Vspr | P_ClearanceCtrEnable | bool | false | true |  |  | false |  | false | false | C |  | P_ClearanceCtrEnable | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_StaticClearance | Vspr | P_StaticClearance | float | 0 | 100 |  |  | 22.81 |  | 22.8741 | 22.8741 | C |  | P_StaticClearance | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_ClearanceDeviation | Vspr | P_ClearanceDeviation | float | 0 | 100 |  |  | 1 |  | 1 | 1 | C |  | P_ClearanceDeviation | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_ClearanceThreshold | Vspr | P_ClearanceThreshold | float | 0 | 100 |  |  | 8.5 |  | 10.5 | 10.5 | C |  | P_ClearanceThreshold | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_ClearanceAzimuthTol | Vspr | P_ClearanceAzimuthTol | float | 0 | 100 |  |  | 0.26181 |  | 0.08727 | 0.08727 | C |  | P_ClearanceAzimuthTol | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_AuxPitchAngle | Vspr | P_AuxPitchAngle | float | 0 | 100 |  |  | 0.0349 |  | 0.01745 | 0.01745 | C |  | P_AuxPitchAngle | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_AuxTimeLength | Vspr | P_AuxTimeLength | float | 0 | 100 |  |  | 12 |  | 20 | 20 | C |  | P_AuxTimeLength | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_AuxIncreaseTime | Vspr | P_AuxIncreaseTime | float | 0 | 100 |  |  | 1 |  | 2 | 2 | C |  | P_AuxIncreaseTime | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
P_AuxDecreaseTime | Vspr | P_AuxDecreaseTime | float | 0 | 100 |  |  | 10 |  | 4 | 4 | C |  | P_AuxDecreaseTime | Param.Algorithm.DynGenSpeed |  | Observer | Administrator
;Noise Control
P_NoiseControlCalEnable | Vspr | calculation enable | bool | false | true |  |  | false | √ |  |  | C |  | Long Avg Cycle Time Mismatch Factor | Param.Algorithm.NoiseControl | - | Observer | Administrator
P_NoiseControlOutputEnable | Vspr | output enable, if calculation disable, this also disable | bool | false | true |  |  | false | √ |  |  | C |  | Long Avg Cycle Time Mismatch Factor | Param.Algorithm.NoiseControl | - | Observer | Administrator
P_NoiseControlWindMoveAverageTimeShort | Vspr | one order filter time for wind speed, short | float | 0 | 600 |  |  | 5 |  |  |  | C |  |  | Param.Algorithm.NoiseControl | s | Observer | Administrator
P_NoiseControlWindMoveAverageTimeLong | Vspr | one order filter time for wind speed, long | float | 0 | 600 |  |  | 10 |  |  |  | C
P_NoiseControlSpeedMoveAverageTimeShort | Vspr | one order filter time for rotor speed, short | float | 0 | 600 |  |  | 0.5 |  |  |  | C |  |  | Param.Algorithm.NoiseControl | s | Observer | Administrator
P_NoiseControlWindSpeed | Vspr | wind noise is bigger than wtg, m/s | float | 0 | 30 |  |  | 14 |  |  |  | C |  |  | Param.Algorithm.NoiseControl | s | Observer | Administrator
P_NoiseControlSpeedmax | Vspr | max rotor speed limit under noise control | float | 0 | 300 |  |  | 1.2566 |  |  |  | C |  |  | Param.Algorithm.NoiseControl | rad/s | Observer | Administrator
P_NoiseControlPowermax | Vspr | max shaft power limit under noise control | float | 0 | 4000000 |  |  | 3834000 |  |  |  | C |  |  | Param.Algorithm.NoiseControl | w | Observer | Administrator
P_NoiseControlRotorSpeedCheckMargin | Vspr | RotorSpeedCheckMargin, rad/s | float | 0 | 10 |  |  | 0.01047 |  |  |  | C |  |  | Param.Algorithm.NoiseControl |  | Observer | Administrator
P_NoiseControlPitchAngleCheckMargin | Vspr | PitchAngleCheckMargin, rad | float | 0 | 1 |  |  | 0.0017452 |  |  |  | C |  |  | Param.Algorithm.NoiseControl |  | Observer | Administrator
P_NoiseControlStateKeepTime | Vspr | from low level to high level timer, s | float | 0 | 100 |  |  | 20 |  |  |  | C |  |  | Param.Algorithm.NoiseControl |  | Observer | Administrator
P_NoiseControlPitchSetpointLowpassTime | Vspr |  | float | 0 | 1000 |  |  | 25 |  |  |  | C |  |  | Param.Algorithm.NoiseControl |  | Observer | Administrator
Note on I2: Francesco Vanni: This column contains default values appropriate for the 2MW demo turbine. It should be removed and the other "Initial Value" column should be uncommented. Red = values which have to be set for controller to run. Black+bold = the controller will run with these settings, but they should be changed before delivering the controller. Black = these settings may be left to the default value but have to be reviewed before delivery.
Note on K2: Francesco Vanni: This column contains default values appropriate for the 2MW demo turbine. It should be removed and the other "Initial Value" column should be uncommented. Red = values which have to be set for controller to run. Black+bold = the controller will run with these settings, but they should be changed before delivering the controller. Black = these settings may be left to the default value but have to be reviewed before delivery.
Note on A5: 赵树椿: 额定转速 单位：rad/s
Note on A7: 赵树椿: 额定轴功率 单位：W
Note on A8: 赵树椿: 最优桨距角 单位：rad
Note on A10: 赵树椿: 最小变桨速率 单位：rad/s
Note on A11: 赵树椿: 最大变桨速率 单位：rad/s
Note on A21: Windows 用户: 基于X方向加速度限功率 By 田萌
Note on A25: Windows 用户: 高湍流限功率 By 李永明
Note on A31: Windows 用户: 高风速限功率（暴风算法） By 李永明
Note on A32: Windows 用户: 高风速限功率（暴风算法） By 李永明
Note on A36: 赵树椿: 最小转速 单位：rad/s
Note on A51: 赵树椿: 最小转速 单位：rad/s
Note on A59: 赵树椿: 正常停机速率 单位：rad/s
Note on A60: 赵树椿: 快速停机速率 单位：rad/s
Note on A62: 赵树椿: 慢速停机速率 单位：rad/s
Note on A65: 赵树椿: 电网掉电停机速率 单位：rad/s
Note on A66: 赵树椿: 开启Rsafe的时间，0为不开启 单位：s
Note on A70: 赵树椿: N4 单位：rad/s
Note on A75: 赵树椿: 变桨需求合理性验证的转速，一般设置为额定转速 单位：rad/s
Note on A78: 赵树椿: 软件保护的最小桨距角，一般设置为最优桨距角-2deg 单位：rad
Note on A81: 赵树椿: 最小变桨位置需求角度，一般设置为最优桨距角-2deg 单位：rad
Note on A90: 赵树椿: 低桨距角过速保护的转速水平，一般设置为1.05*Nr 单位：rad/s
Note on I96: 赵树椿: 默认关闭该保护，主控程序中开启。
Note on A110: 赵树椿: 叶轮半径，单位：m
Note on A123: 赵树椿: 最大发电机扭矩，一般设置为1.1*额定扭矩 单位：N
Note on A142: 赵树椿: 最优增益
Note on A173: 赵树椿: 最大变桨加速度 单位：rad/s^2
Note on A174: 赵树椿: 最大变桨速度 单位：rad/s
Note on A271: Windows 用户: 杨晓修改
Note on A274: Windows 用户: By杨晓
Note on A280: Windows 用户: By赵树椿

## Filters
;
Name | Description en_GB | Display Name | Enabled | Numerator Type | Denominator Type | Numerator TC | Denominator TC | Numerator Frequency | Numerator Damping Ratio | Denominator Frequency | Denominator Damping Ratio | W0 | Prewarping Wc
;
F_PitchSpeedFilters | Pitch-speed loop shaping filters | 1 | 1 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 7.87 | 1 | 0 | 0
|  | 2 | 1 | SecondOrder | SecondOrder | 0 | 0 | 1.49 | 0.01 | 1.49 | 0.1 | 0 | 0
|  | 3 | 1 | SecondOrder | SecondOrder | 0 | 0 | 3.7071 | 0.02 | 3.7071 | 0.2 | 1.2357 | 0
|  | 4 | 1 | SecondOrder | SecondOrder | 0 | 0 | 9.8779 | 0.014 | 9.8779 | 0.14 | 0 | 0
|  | 5 | 1 | SecondOrder | SecondOrder | 0 | 0 | 6.6434 | 0.03 | 6.6434 | 0.3 | 0 | 0
|  | 6 | 1 | SecondOrder | SecondOrder | 0 | 0 | 15.511 | 0.013 | 15.511 | 0.13 | 0 | 0
|  | 7 | 1 | SecondOrder | SecondOrder | 0 | 0 | 7.4142 | 0.1 | 7.4142 | 0.4 | 1.2357 | 0
|  | 8 | 1 | SecondOrder | SecondOrder | 0 | 0 | 22.737 | 0.015 | 22.737 | 0.15 | 0 | 0
F_TorqueSpeedFilters | Torque-speed loop shaping filters | 1 | 1 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 7.87 | 1 | 0 | 0
|  | 2 | 1 | SecondOrder | SecondOrder | 0 | 0 | 1.49 | 0.01 | 1.49 | 0.1 | 0 | 0
|  | 3 | 1 | SecondOrder | SecondOrder | 0 | 0 | 3.7071 | 0.03 | 3.7071 | 0.23 | 1.2357 | 0
|  | 4 | 1 | SecondOrder | SecondOrder | 0 | 0 | 15.511 | 0.03 | 15.511 | 0.3 | 0 | 0
|  | 5 | 1 | SecondOrder | SecondOrder | 0 | 0 | 9.8779 | 0.0366 | 9.8779 | 0.366 | 0 | 0
|  | 6 | 1 | SecondOrder | SecondOrder | 0 | 0 | 6.6434 | 0.04 | 6.6434 | 0.4 | 0 | 0
|  | 7 | 1 | SecondOrder | SecondOrder | 0 | 0 | 7.4142 | 0.1 | 7.4142 | 0.4 | 1.2357 | 0
|  | 8 | 1 | SecondOrder | SecondOrder | 0 | 0 | 22.737 | 0.05 | 22.737 | 0.5 | 0 | 0
F_ConstantPowerFilters | Constant power loop shaping filters | 1 | 1 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 7.87 | 1 | 0 | 0
|  | 2 | 1 | SecondOrder | SecondOrder | 0 | 0 | 1.49 | 0.01 | 1.49 | 0.1 | 0 | 0
|  | 3 | 1 | SecondOrder | SecondOrder | 0 | 0 | 3.7071 | 0.03 | 3.7071 | 0.23 | 1.2357 | 0
|  | 4 | 1 | SecondOrder | SecondOrder | 0 | 0 | 15.511 | 0.03 | 15.511 | 0.3 | 0 | 0
|  | 5 | 1 | SecondOrder | SecondOrder | 0 | 0 | 9.8779 | 0.0366 | 9.8779 | 0.366 | 0 | 0
|  | 6 | 1 | SecondOrder | SecondOrder | 0 | 0 | 6.6434 | 0.04 | 6.6434 | 0.4 | 0 | 0
|  | 7 | 1 | SecondOrder | SecondOrder | 0 | 0 | 7.4142 | 0.1 | 7.4142 | 0.4 | 1.2357 | 0
|  | 8 | 1 | SecondOrder | SecondOrder | 0 | 0 | 22.737 | 0.05 | 22.737 | 0.5 | 0 | 0
F_NacelleAccFAFilters | Nacelle acceleration loop shaping filters | 1 | 0 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 5 | 0.8 | 0 | 0
|  | 2 | 0 | SecondOrder | SecondOrder | 0 | 0 | 11.5926 | 0.03 | 11.5926 | 0.2 | 1.2357 | 0
|  | 3 | 0 | SecondOrder | SecondOrder | 0 | 0 | 3.8642 | 0.03 | 3.8642 | 0.23 | 1.2357 | 0
|  | 4 | 0 | SecondOrder | SecondOrder | 0 | 0 | 7.7283 | 0.03 | 7.7283 | 0.32 | 1.2357 | 0
|  | 5 | 0 | SecondOrder | SecondOrder | 0 | 0 | 0.69981 | 0.2348 | 0.69981 | 0.5 | 0 | 0
|  | 6 | 0 | SecondOrder | SecondOrder | 0 | 0 | 1.3682 | 0.2038 | 1.3681 | 0.5 | 0 | 0
|  | 7 | 0 | FirstOrder | FirstOrder | 0.6371 | 2.0765 | 10.05 | 0.05 | 10.05 | 0.35 | 0 | 0
|  | 8 | 0 | SecondOrder | SecondOrder | 0 | 0 | 10.05 | 0.05 | 10.05 | 0.35 | 0 | 0
F_NacelleAccFAFiltersForPitchSchedule | Nacelle acceleration loop shaping filters | 1 | 0 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
|  | 2 | 0 | SecondOrder | SecondOrder | 0 | 0 | 1.8850 | 0.05 | 1.8850 | 0.50 | 0 | 0
|  | 3 | 0 | SecondOrder | SecondOrder | 0 | 0 | 3.7699 | 0.05 | 3.7699 | 0.50 | 0 | 0
|  | 4 | 0 | SecondOrder | SecondOrder | 0 | 0 | 0.565 | 0.554 | 5.28 | 0.698 | 0 | 0
F_DriveTrainDamperFilters | Drive-train damper filters | 1 | 0 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 12.3923 | 0.76958 | 0 | 0
|  | 2 | 0 | FirstOrderPlusDiff | SecondOrder | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F_IpcFilters | IPC loop shaping filters | 1 | 0 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 15 | 0.707 | 0 | 0
|  | 2 | 0 | SecondOrder | SecondOrder | 0 | 0 | 3.3615 | 0.02 | 3.3615 | 0.4 | 1.2357 | 0
|  | 3 | 0 | SecondOrder | SecondOrder | 0 | 0 | 6.723 | 0.02 | 6.723 | 0.4 | 1.2357 | 0
F_2PIpcFilters | 2P IPC loop shaping filters | 1 | 0 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 15 | 0.707 | 0 | 0
|  | 2 | 0 | SecondOrder | SecondOrder | 0 | 0 | 3.3615 | 0.02 | 3.3615 | 0.4 | 1.2357 | 0
|  | 3 | 0 | SecondOrder | SecondOrder | 0 | 0 | 6.723 | 0.02 | 6.723 | 0.4 | 1.2357 | 0
F_PitchActuator | Pitch actuator dynamic model | 1 | 1 | ZeroOrder | FirstOrder | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0
F_NacelleAxLoopShaping | Nacelle ax loopshaping for NL schedule | 1 | 0 | ZeroOrder | SecondOrder | 0 | 0 | 0 | 0 | 3.1416 | 0.7 | 0 | 0
F_ShaftPowerShaping | Powershaping for shaft power used for iAboverated (can be used as mov) | 0 | 0 | ZeroOrder | FirstOrder | 0 | 0.2 | 0 | 0 | 0.0 | 0.0 | 0 | 0

## Schedules
;
Name | Description en_GB | Enabled | Display Name | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
;
T_PitchSpeedProportionalGain | Pitch-speed proportional gain schedule | 1 | Pitch | 0.0393 | 0.0695 | 0.133 | 0.2101 | 0.2616 | 0.3194
|  |  | Kp | 0.9817 | 0.82517 | 0.6022 | 0.4856 | 0.4474 | 0.4020
T_PitchSpeedProportionalGainFast | Pitch-speed proportional gain schedule Slow | 1 | Pitch | 0.0393 | 0.0695 | 0.133 | 0.2101 | 0.2616 | 0.3194
|  |  | Kp | 0.9817 | 0.82517 | 0.6022 | 0.4856 | 0.4474 | 0.4020
T_PitchSpeedIntegralGain | Pitch-speed integral gain schedule | 0 | Pitch | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Ki | 0 | 0 | 0 | 0 | 0 | 0
T_PitchSpeedIntegralGainFast | Pitch-speed integral gain schedule Slow | 0 | Pitch | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Ki | 0 | 0 | 0 | 0 | 0 | 0
T_PitchSpeedIntegralTimeConstant | Pitch-speed integral time-constant schedule | 1 | Pitch | 0.0393 | 0.0695 | 0.133 | 0.2101 | 0.2616 | 0.3194
|  |  | Ti | 17.13 | 15.4373 | 12.8116 | 10.7987 | 8.9388 | 7.9388
T_PitchSpeedIntegralTimeConstantFast | Pitch-speed integral time-constant schedule Slow | 1 | Pitch | 0.0393 | 0.0695 | 0.133 | 0.2101 | 0.2616 | 0.3194
|  |  | Ti | 17.13 | 15.4373 | 12.8116 | 10.7987 | 8.9388 | 7.9388
T_PitchSpeedDerivativeGainSchedule | Pitch-speed derivative gain schedule | 1 | Pitch | 0.0393 | 0.0695 | 0.133 | 0.2101 | 0.2616 | 0.3194
|  |  | Kd | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05
T_PitchSpeedDerivativeGainScheduleFast | Pitch-speed derivative gain schedule | 1 | Pitch | 0.0393 | 0.0695 | 0.133 | 0.2101 | 0.2616 | 0.3194
|  |  | Kd | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3
T_ErrorSchedule | Pitch-speed non-linear error gain schedule | 0 | EEdot | 0: 0.0015; 1: 0.003
|  |  | GainFactor | 0: 1; 1: 2
T_EEdotThresholdOnPitch | EEdot threshold on pitch beyond which a pitch kick is triggered | 1 | Pitch | 0: 0; 1: 0.0698; 2: 0.1745; 3: 0.2618; 4: 0.3491
|  |  | Threshold | 0: 0.00047; 1: 0.001; 2: 0.0028; 3: 0.0035; 4: 0.0035
T_NacelleAccFASched | Nacelle acceleration gain schedule | 0 | Point | 0: 0; 1: 0; 2: 0; 3: 0
|  |  | GainFactor | 0: 0; 1: 0; 2: 0; 3: 0
T_FinePitchSchedule | Fine Pitch schedule | 1 | Power | 0: 2000000; 1: 2760553.8
|  |  | FinePitch | 0: 0; 1: 0.04363
T_FinePitchScheduleYaw | Fine Pitch schedule yaw | 1 | YawFraction | 0: 0.7; 1: 1
|  |  | FinePitch | 0: 0; 1: 0.04365
T_DynamicFinePitch | Dynamic fine pitch vs pitch angle lookup table | 0 | Pitch | 0: -0.008727; 1: 0.0873; 2: 0.1396; 3: 0.1745; 4: 0.3491
|  |  | DynamicFinePitch | 0: -0.008727; 1: 0.0349; 2: 0.0698; 3: 0.0873; 4: 0.1047
T_FinePitchScheduleNacAccX | Fine pitch vs Nacelle accleration X lookup table | 0 | Nacelleaccx | 0: 0.12; 1: 0.15
|  |  | FinePitch | 0: 0; 1: 0.08727
T_FinePitchScheduleNacAccXThreshold | Fine pitch schedule threshold against wind speed | 0 | windspeed | 0: 5; 1: 7; 2: 9; 3: 13; 4: 15
|  |  | Nacelleaccxthreshold | 0: 0.3; 1: 0.15; 2: 0.135; 3: 0.166; 4: 0.2
T_TorqueSpeedLimit | Torque limit vs. generator speed lookup table | 0 | GeneratorSpeed | 0: 0; 1: 0; 2: 0
|  |  | TorqueLimit | 0: 0; 1: 0; 2: 0
T_DamperLimitSched | Normalised drive-train damper torque limit lookup table | 1 | TorqueSetpoint | 0: 0; 1: 0.3
|  |  | TorqueLimit | 0: 0; 1: 1
T_StartupPitchWindSchedule | Safe start minimum pitch angle vs. wind speed lookup table | 1 | WindSpeed | 0: 3; 1: 5; 2: 25; 3: 30
|  |  | Pitch | 0: 0.035; 1: 0.1; 2: 0.5; 3: 1.5
T_StartupPitchTSRSchedule | Startup pitch limit vs. tip speed ratio lookup table | 1 | TSR | 0: 0.3; 1: 1; 2: 4
|  |  | Pitch | 0: 1.3963; 1: 0.69813; 2: 0
T_Pitchmin1 | Startup Pitch Limit | 1 | speed | 0: 0; 1: 0.4189
|  |  | pitchangle | 0: 0.209; 1: 0
T_IpcMaximumPitchTorqueSchedule | IPC maximum pitch limit vs. torque setpoint lookup table | 0 | NormTorque | 0: 0.65; 1: 1
|  |  | PitchFactor | 0: 0; 1: 1
T_IpcMaximumPitchGenAccSchedule | IPC maximum pitch limit vs. generator acceleration lookup table | 0 | GeneratorAcceleration | 0: 0.025; 1: 0.035; 2: 0.04
|  |  | PitchFactor | 0: 1; 1: 0.5; 2: 0
T_IpcMinimumPitchPitchSchedule | IPC minimum pitch limit vs. pitch angle lookup table | 0 | Pitch | 0: 0; 1: 2.5; 2: 5
|  |  | PitchFactor | 0: 0.25; 1: 0.3; 2: 1
T_IpcMaximumPitchPitchSchedule | IPC maximum pitch limit vs. pitch angle lookup table | 0 | Pitch | 0: 0.28; 1: 0.43; 2: 0.69
|  |  | PitchFactor | 0: 1; 1: 0.7; 2: 0
T_IpcMaximumPitchPitchRateSchedule | IPC maximum pitch limit schedule on collective pitch rate | 0 | PitchRate | 0: 0.0524; 1: 0.0873
|  |  | PitchFactor | 0: 1; 1: 0.5
T_IpcMinimumPitchYawErrorSchedule | IPC minimum pitch limit vs. yaw error ratio lookup table | 0 | YawErrorRatio | 0: 0; 1: 0.7; 2: 0.8
|  |  | PitchFactor | 0: 0; 1: 0; 2: 1
T_2PIpcGainSchedOnRateAmplitude | 2P IPC PID acrGS scheduling based on max pitch rate demands | 0 | MaxPitchRate | 0: 0.096; 1: 0.114; 2: 0.122
|  |  | GsFactor | 0: 1; 1: 0.25; 2: 0
T_HighYawErrorThresholdSchedule | Yaw error threshold vs. wind speed lookup table | 1 | WindSpeed | 0: 0; 1: 5; 2: 10.0; 3: 35
|  |  | YawError | 0: 1.571; 1: 1.047; 2: 0.785; 3: 0.523
T_NacAccXDeratingThreshold | Nacelle acceleration fore-aft vs. wind speed lookup table | 0 | windspeed | 0: 5; 1: 7; 2: 9; 3: 13
|  |  | NacAccX | 0: 0.3; 1: 0.3; 2: 0.3; 3: 0.3
T_HighWindPowerLimitFactorSchedule | Power Limit Factor vs. wind speed lookup table | 0 | WindSpeed | 0: 0; 1: 14; 2: 15; 3: 20
|  |  | SpeedFacor | 0: 1; 1: 1; 2: 1; 3: 0.6
T_HighWindSpeedLimitFactorSchedule | Speed Limit Factor vs. wind speed lookup table | 0 | WindSpeed | 0: 0; 1: 16.0; 2: 19.0; 3: 23.0
|  |  | SpeedFacor | 0: 1; 1: 1; 2: 1; 3: 0.68
T_GentlePitchDropSchedule | Pitch drop angle limit lookup table | 0 | Pitch | 0: -0.01745; 1: 0.0873; 2: 0.1745; 3: 0.3491; 4: 0.4363
|  |  | PitchDropLimit | 0: 0.1745; 1: 0.1745; 2: 0.0873; 3: 0.0349; 4: 0.0349
T_FastShutdownTorque | Fast Shutdown torque vs. speed lookup table | 1 | GeneratorSpeed | 0: 0.6282; 1: 1.1; 2: 1.2357; 3: 1.482; 4: 1.681
|  |  | Torque | 0: 0; 1: 2234000; 2: 2234000; 3: 1862721; 4: 0
T_NormalShutdownPitchrate |  | 1 | Pitch | -0.01745 | 0.0873 | 0.3142 | 0.4712 | 0.5236 | 1.571
|  |  | PitchRate | 0.0349 | 0.0349 | 0.0349 | 0.0349 | 0.0349 | 0.0349
T_NormalShutdownPitchrate2 | T_NormalShutdownPitchrate2 | 0 | GeneratorSpeed | 0: 0.6074; 1: 0.7; 2: 1.2; 3: 1.256; 4: 1.366
|  |  | PitchRate | 0: 0.0349; 1: 0.01; 2: 0.01; 3: 0.01; 4: 0.0349
T_NormalShutdownTorque | Normal Shutdown torque vs. power lookup table | 0 | PowerSetpoint | 0: 0; 1: 267706; 2: 1894804
|  |  | Torque | 0: 0; 1: 313570; 2: 1397780
T_GridLossShutdownPitchRate | Grid Loss Shutdown Pitch Rate lookup table | 1 | Pitch | 0: 0.08726; 1: 0.08726; 2: 0.694; 3: 0.694
|  |  | PitchRate | 0: 0.0349; 1: 0.01745; 2: 0.01745; 3: 0.0349
T_GridLossShutdownTorque | GridLoss Shutdown torque vs. time lookup table | 1 | Time | 0: 0; 1: 4
|  |  | Torque | 0: 13376; 1: 0
T_LvrtPitchKickRate | LVRT pitch kick rate vs. pitch angle schedule | 1 | Pitch | 0: 0; 1: 0.087266; 2: 0.2618; 3: 0.43633
|  |  | PitchRate | 0: 0.10472; 1: 0.10472; 2: 0.05236; 3: 0.05236
T_NonLinearNacelleAccelerationThreshold |  | 1 | Pitch | 0: 0.071148; 1: 0.17025; 2: 0.28619; 3: 0.38516
|  |  | Threshold | 0: 0.82466; 1: 1.0792; 2: 1.6635; 3: 2.4066
T_LinearRegressionMinFiltSpeedErrorOnPitch_coeff |  | 0 | Coeff | 0: -0.065; 1: -0.022
|  |  | Order | 0: 1; 1: 0
T_NonLinearNL2Threshold |  | 0 | Pitch | -0.008727 | -0.0082 | 0.0063 | 0.1255 | 0.3005 | 0.3911 | 0.422 | 0.6109
|  |  | Threshold | 0.0017 | 0.0017 | 0.0017 | 0.003 | 0.0061 | 0.0091 | 0.0119 | 0.0119
T_NonLinearGenAccThresholdAfterDelay |  | 0 | Pitch | -0.008727 | 0.0049 | 0.1072 | 0.2869 | 0.3859 | 0.4197 | 0.6109
|  |  | Threshold | 0.0216 | 0.0216 | 0.0213 | 0.0409 | 0.0642 | 0.1066 | 0.1066
T_GenAccPitchAngleThreshold |  | 0 | Pitch | 0: 0; 1: 0.0349; 2: 0.1047; 3: 0.1571; 4: 0.349
|  |  | GenAcc | 0: 0.03; 1: 0.03; 2: 0.045; 3: 0.06; 4: 0.07
T_LidarBeamConfiguration |  | 0 | Zenith | 0: 0.33475; 1: 0.33475; 2: 0.33475; 3: 0.33475
|  |  | Azimuth | 0: 0.69115; 1: 2.4504; 2: -0.69115; 3: -2.4504
T_LidarFocusDistance |  | 0 | EnableFlag | bar: 0 to 7
|  |  | Distance | 45 | 65 | 85 | 105 | 125 | 145 | 165 | 185
T_WsDthetaDv0 |  | 0 | windspeed | 3 | 9.1 | 9.2 | 9.3 | 9.5 | 10.5 | 13 | 22
|  |  | DthetaDv0 | 0 | 0 | 0.0421 | 0.17472 | 0.09192 | 0.04588 | 0.02934 | 0.01913
T_GRTThreshold | windspeed vs GRTPitchKick GustArea lookup table | 1 | windspeed | 0: 7; 1: 9; 2: 13; 3: 20; 4: 25
|  |  | GustArea | 0: 5.5; 1: 5.5; 2: 5.5; 3: 7; 4: 8
T_GRTPitchKick | GRTPitchKick action vs extrapitchrate lookup table | 1 | GustArea | 0: 3; 1: 5.5; 2: 6; 3: 7; 4: 10
|  |  | extraPitchrate | 0: 0.01396; 1: 0.01396; 2: 0.01396; 3: 0.01396; 4: 0.01396
T_ShearPitchKickThreshold1 | Vertical ShearPitchKick lookup table for positive mode | 1 | ShearArea | 0: 9; 1: 10; 2: 13; 3: 15
|  |  | extraPitchrate | 0: 0.01571; 1: 0.01571; 2: 0.01745; 3: 0.01745
T_ShearPitchKickThreshold2 | Vertical ShearPitchKick lookup table for negtive mode | 1 | ShearArea | 0: -8; 1: -9; 2: -13; 3: -15
|  |  | extraPitchrate | 0: 0.01571; 1: 0.01571; 2: 0.01745; 3: 0.01745
T_ShearPitchKickHThreshold1 | Horizontal ShearPitchKickH lookup table for positive mode | 1 | ShearAreaH | 0: 9; 1: 10; 2: 13; 3: 15
|  |  | extraPitchrate | 0: 0.01571; 1: 0.01571; 2: 0.01745; 3: 0.01745
T_ShearPitchKickHThreshold2 | Horizontal ShearPitchKickH lookup table for negtive mode | 1 | ShearAreaH | 0: -8; 1: -9; 2: -13; 3: -15
|  |  | extraPitchrate | 0: 0.01571; 1: 0.01571; 2: 0.01745; 3: 0.01745
T_StallFinePitchSchedule | Fine Pitch schedule for stall | 0 | Windspeed | 0: 0; 1: 7.9; 2: 8; 3: 10; 4: 10.1
|  |  | FinePitch | 0: -0.008727; 1: -0.008727; 2: 0.03054; 3: 0.03054; 4: -0.008727
T_SpeedUpgradeInStageIII | 风机运行III区域额定转速提升 | 0 | Pitch | 0: 0.0349; 1: 0.0698
|  |  | SpeedRatio | 0: 1.1; 1: 1.0
T_PowerIncreaseFactorSchedule | 风机运行IV区域部分风速段额定功率提升 | 0 | WindSpeed | 0: 11; 1: 14; 2: 17; 3: 20.0
|  |  | PowerFacor | 0: 1; 1: 1.015; 2: 1.01; 3: 1
T_NoiseControlPitchmin |  | 0 | RotorSpeed_RPM | 0 | 11.1 | 11.4 | 11.7 | 12 | 14
|  |  | PitchMin_deg | 0 | 0 | 1 | 2 | 3 | 3

## DISCON Parameters
;
Name | Subsystem | Visibility | Description en_GB | Data Type | Min | Max | Initial Value | Reset Condition
;Configuration for Tests and Simulations
P_DisconStateMachineStartTime | Vspr | Private | Delay in discon state machine start up | float | 0 | 1000 | 20 | C
P_DisconLoggingBufferLength | Vspr | Private | Length of the logging buffer in controller cycles (0 to disable logging) | int | 0 | 1000 | 1000 | C
P_AllBladesAtFeatherTolerance | Vspr | Private | Margin below feather angle within which a blade is considered to be at feather | float | 0 | 1 | 0.005812 | C
P_FaultPitchRunawayRate | Vspr | Private | Pitch rate for collective pitch runaway fault | float | -1 | 1 | -0.0694 | C
P_FaultPitchRunawayLimit | Vspr | Private | Pitch angle limit for collective pitch runaway fault | float | -2 | 2 | -0.08727 | C
P_FaultOverspeedRampRate | Vspr | Private | Speed setpoint ramp rate for overspeed tests | float | 0 | 1 | 0.01 | C
P_LvrtTorqueStartingValue | Vspr | Private | Torque available at the beginning of a LVRT event (for testing only - should be provided by PCS via a CI_ channel) | float | 0 | 10000000000 | 0 | C

## DISCON Mappings
; |  | Discon interface (Bladed 4.4 and older) |  | External controller API interface (Bladed 4.4 and newer)
Channel Name | Delay | Discon Name | Discon Expression | API Name | API Expression
; |  | ;
AllBladesAtFeather_Input |  | CI_AlgAllBladesAtFeather | avrSwap[3] > (P_GetPositiveFeatherAngle()-P_GetAllBladesAtFeatherTolerance()) && avrSwap[32] > (P_GetPositiveFeatherAngle()-P_GetAllBladesAtFeatherTolerance()) && avrSwap[33] > (P_GetPositiveFeatherAngle()-P_GetAllBladesAtFeatherTolerance()) | CI_AlgAllBladesAtFeather | GetMeasuredPitchAngle(turbine_id,0) > (P_GetPositiveFeatherAngle() - P_GetAllBladesAtFeatherTolerance()) && GetMeasuredPitchAngle(turbine_id,1) > (P_GetPositiveFeatherAngle()-P_GetAllBladesAtFeatherTolerance()) && GetMeasuredPitchAngle(turbine_id,2) > (P_GetPositiveFeatherAngle()-P_GetAllBladesAtFeatherTolerance())
ElectricalTorque_Input |  | CI_AlgElectricalTorque | avrSwap[22] | CI_AlgElectricalTorque | (float) GetMeasuredGeneratorTorque(turbine_id)
GeneratorSpeed_Input | 0.02 | CI_AlgGeneratorSpeed | avrSwap[19] | CI_AlgGeneratorSpeed | (float) GetMeasuredGeneratorSpeed(turbine_id)
RealPower_Input |  | CI_AlgRealPower | avrSwap[14] | CI_AlgRealPower | (float) GetMeasuredElectricalPowerOutput(turbine_id)
ShaftPower_Input |  | CI_AlgShaftPower | avrSwap[13] | CI_AlgShaftPower | (float) GetMeasuredShaftPower(turbine_id)
PcsSynchronised_Input |  | CI_AlgPcsSynchronised | int(avrSwap[34]) != 0 | CI_AlgPcsSynchronised | GetGeneratorContactor(turbine_id) != 0
PitchPosition1_Input |  | CI_AlgPitchPosition1 | avrSwap[3] | CI_AlgPitchPosition1 | (float) GetMeasuredPitchAngle(turbine_id,0)
PitchPosition2_Input |  | CI_AlgPitchPosition2 | avrSwap[32] | CI_AlgPitchPosition2 | (float) GetMeasuredPitchAngle(turbine_id,1)
PitchPosition3_Input |  | CI_AlgPitchPosition3 | avrSwap[33] | CI_AlgPitchPosition3 | (float) GetMeasuredPitchAngle(turbine_id,2)
NacelleForeAftAcceleration_Input | 0.02 | CI_AlgNacelleForeAftAcceleration | avrSwap[52] | CI_AlgNacelleForeAftAcceleration | (float) GetMeasuredTowerTopForeAftAcceleration(turbine_id)
NacelleSideSideAcceleration_Input |  | CI_AlgNacelleSideSideAcceleration | avrSwap[53] | CI_AlgNacelleSideSideAcceleration | (float) GetMeasuredTowerTopSideSideAcceleration(turbine_id)
AverageWindSpeed_Input |  | CI_AlgAverageWindSpeed | avrSwap[26] | CI_AlgAverageWindSpeed | (float) GetNominalHubFlowSpeed(turbine_id)
RotorAzimuth_Input | 0.02 | CI_AlgRotorAzimuth | avrSwap[59] | CI_AlgRotorAzimuth | (float) GetMeasuredRotorAzimuthAngle(turbine_id)
YawError_Input |  | CI_AlgYawError | avrSwap[23] | CI_AlgYawError | (float) GetMeasuredYawError(turbine_id)
NormalShutdown_Input |  | CI_AlgNormalShutdown | (CO_GetAlgNormalShutdown() ¦¦ int(avrSwap[116]) == 4) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup) | CI_AlgNormalShutdown | (CO_GetAlgNormalShutdown() ¦¦ GetControllerState(turbine_id) == 4) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup)
SlowShutdown_Input |  | CI_AlgSlowShutdown | CO_GetAlgSlowShutdown() && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup) | CI_AlgSlowShutdown | (CO_GetAlgSlowShutdown()) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup)
FastShutdown_Input |  | CI_AlgFastShutdown | (CO_GetAlgFastShutdown() ¦¦ CO_GetAlgAutonomousFeather() ) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup) | CI_AlgFastShutdown | (CO_GetAlgFastShutdown() ¦¦ CO_GetAlgAutonomousFeather()) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup)
GridLossShutdown_Input |  | CI_AlgGridLossShutdown | (CO_GetAlgGridLossShutdown() ¦¦ int(avrSwap[160]) == 5) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup) | CI_AlgGridLossShutdown | (CO_GetAlgGridLossShutdown() ¦¦ GetControllerFailureFlag(turbine_id) == 5) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup)
AlgorithmReset_Input |  | CI_AlgAlgorithmReset | (int(avrSwap[96]) == 1) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup) | CI_AlgAlgorithmReset | (GetActiveSafetySystemNumber(turbine_id) == 1) && (S_GetVsprState() != VsprWaitForStartupEnter) && (S_GetVsprState() != VsprWaitForStartup)
PcsVoltageDip_Input |  | CI_AlgPcsVoltageDip | avrSwap[112] > 0.0f | CI_AlgPcsVoltageDip | (float) GetNetworkVoltageDisturbanceFactor(turbine_id) > 0.0f
PcsVoltageDipTorqueLimit_Input |  | CI_AlgPcsVoltageDipTorqueLimit | P_GetLvrtTorqueStartingValue() | CI_AlgPcsVoltageDipTorqueLimit | P_GetLvrtTorqueStartingValue()
SpeedSetpointLimit_Input |  | CI_AlgSpeedSetpointLimit | P_GetRatedGeneratorSpeed() | CI_AlgSpeedSetpointLimit | P_GetRatedGeneratorSpeed()
PowerSetpointLimit_Input |  | CI_AlgPowerSetpointLimit | P_GetSteadyShaftPowerLimit() | CI_AlgPowerSetpointLimit | P_GetSteadyShaftPowerLimit()
MinimumPitchAngle_Input |  | CI_AlgMinimumPitchAngle | P_GetMinimumFinePitch() | CI_AlgMinimumPitchAngle | P_GetMinimumFinePitch()
BladeLoadsOk_Input |  | CI_AlgBladeLoadsOk | true | CI_AlgBladeLoadsOk | true
OutOfPlaneBendingMoment1_Input | 0.08 | CI_AlgOutOfPlaneBendingMoment1 | avrSwap[29] | CI_AlgOutOfPlaneBendingMoment1 | (float) GetMeasuredBladeOutOfPlaneBendingMoment(turbine_id,0)
OutOfPlaneBendingMoment2_Input | 0.08 | CI_AlgOutOfPlaneBendingMoment2 | avrSwap[30] | CI_AlgOutOfPlaneBendingMoment2 | (float) GetMeasuredBladeOutOfPlaneBendingMoment(turbine_id,1)
OutOfPlaneBendingMoment3_Input | 0.08 | CI_AlgOutOfPlaneBendingMoment3 | avrSwap[31] | CI_AlgOutOfPlaneBendingMoment3 | (float) GetMeasuredBladeOutOfPlaneBendingMoment(turbine_id,2)
SafetySystemTrigger |  |  |  | CI_SafetySystemTrigger | (GetActiveSafetySystemNumber(turbine_id) == 1) ¦¦ (GetActiveSafetySystemNumber(turbine_id) == 2)
Blade1StationPositionX_Input | 0.02 |  |  | CI_MeasuredBlade1StationPositionX | (float) GetMeasuredBladeStationPositionX(turbine_id,0,0)
Blade2StationPositionX_Input | 0.02 |  |  | CI_MeasuredBlade2StationPositionX | (float) GetMeasuredBladeStationPositionX(turbine_id,1,0)
Blade3StationPositionX_Input | 0.02 |  |  | CI_MeasuredBlade3StationPositionX | (float) GetMeasuredBladeStationPositionX(turbine_id,2,0)
; |  | ;
DemandedGeneratorTorque_Output | 0.02 | avrSwap[46] | CO_GetAlgPcsTorqueDemand() | SetDemandedGeneratorTorque(turbine_id, (double) | CO_GetAlgPcsTorqueDemand()
DemandedPitchRateOrPosition1_Output | 0.06 | avrSwap[41] | P_GetPitchActuatorType() ? CO_GetAlgPitchRateDemand1() : CO_GetAlgPitchPositionDemand1() | SetDemandedPitchRateOrPosition(turbine_id,0, (double) | P_GetPitchActuatorType() ? CO_GetAlgPitchRateDemand1() : CO_GetAlgPitchPositionDemand1()
DemandedPitchRateOrPosition2_Output | 0.06 | avrSwap[42] | P_GetPitchActuatorType() ? CO_GetAlgPitchRateDemand2() : CO_GetAlgPitchPositionDemand2() | SetDemandedPitchRateOrPosition(turbine_id,1, (double) | P_GetPitchActuatorType() ? CO_GetAlgPitchRateDemand2() : CO_GetAlgPitchPositionDemand2()
DemandedPitchRateOrPosition3_Output | 0.06 | avrSwap[43] | P_GetPitchActuatorType() ? CO_GetAlgPitchRateDemand3() : CO_GetAlgPitchPositionDemand3() | SetDemandedPitchRateOrPosition(turbine_id,2, (double) | P_GetPitchActuatorType() ? CO_GetAlgPitchRateDemand3() : CO_GetAlgPitchPositionDemand3()
DemandedCollectivePitchAngle_Output | 0.06 | avrSwap[44] | CO_GetAlgPitchPositionDemand1() | SetDemandedCollectivePitchAngle(turbine_id, (double) | CO_GetAlgPitchPositionDemand1()
DemandedCollectivePitchRate_Output |  | avrSwap[45] | P_GetMaximumPitchRateLimit() | SetDemandedCollectivePitchRate(turbine_id, (double) | P_GetMaximumPitchRateLimit()
GeneratorContactor_Output |  | avrSwap[34] | CO_GetAlgPcsSynchroniseRequest() ? 1.0f : 0.0f | SetGeneratorContactor(turbine_id, | CO_GetAlgPcsSynchroniseRequest() ? 1 : 0
ActiveSafetySystemNumber_Output |  | avrSwap[97] | avrSwap[1] > P_GetDisconStateMachineStartTime() ? (CO_GetAlgAutonomousFeather() ? 2.0f : 0.0f) : 0.0f | SetActiveSafetySystemNumber(turbine_id, | GetSimulationCurrentTime(turbine_id) > P_GetDisconStateMachineStartTime() ? (CO_GetAlgAutonomousFeather() ? 2 : 0) : 0